## Final
Name of City / Utility: 2021 Validated Water Audit | WSID Number | Service County | Water System Service Population | Volume From Own Sources | Water Imported | Water Exported | Water Supplied | Billed Metered | Billed Unmetered | Unbilled Metered | Unbilled Unmetered | Authorized Consumption | Water Losses | Annual Volume of Apparent Losses | Annual Volume of Real Losses | Non Revenue Water | Length of Mains | Number of Active and Inactive Service Connections | Average Operating Pressure | Total Annual Cost of Operating Water System | Customer Retail Unit Cost | Variable Production Cost | Unavoidable Annual Real Losses (UARL) vol/Yr | Annual Volume of NRW | Annual Cost of Apparent Losses | Annual Cost of Real Losses | Annual Cost of NRW | Value Applied to Real Losses (VPC / CRUC) | Unit Apparent Losses Vol/conn/day | Unit Real Losses Vol/conn/day | Unit Real Losses per length of main per day | Total Loss Cost Rate $/conn/yr | Apparent Loss Cost Rate $/conn/yr | Real Loss Cost Rate $/conn/yr | Infrastructure Leakage Index (ILI) | Water Audit Data Validity Score | Water Audit Data Validity Tier | Priority Area #1 | Priority Area #2 | Priority Area #3
Adairsville | GA0150000 | Bartow | 7306 | 537.81 | 9.1891 | 111.5514 | 437.4176 | 258.9026 | 0.0036 | 26.2452 | 0.64727 | 285.7987 | 151.6189 | 10.1135 | 141.5054 | 178.5114 | 89.3 | 3331 | 70 | 3295139.79 | 5.86 | 736.88 | 25.1096 | 178.5114 | 55106.84 | 104272.49 | 179195.85 | VPC | 8.3183 | 116.3873 | 4341.3886 | 47.8473 | 16.5436 | 31.3037 | 5.6355 | 76 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Number of Service Connections (Nc)
Adel | GA0750000 | Cook | 6560 | 317.261 | Note 1 | Note 1 | 317.261 | 303.13 | Note 1 | 1.23 | 3.9658 | 308.3258 | 8.9352 | 4.6253 | 4.3099 | 14.131 | 74.5 | 2991 | 54 | 830280 | 2.51 | 3.51 | 16.7869 | 14.13 | 11609.56 | 10817.89 | 22445.69 | CRUC | 4.2367 | 3.9478 | 158.4965 | 7.4983 | 3.8815 | 3.6168 | 0.25674 | 66.1176 | Level III (51-75) | Volume from own sources | Unbilled metered | Variable production cost (applied to Real Losses)
Alamo | GA3090000 | Wheeler | 3650 | 130.837 | Note 1 | Note 1 | 129.5416 | 118.436 | Note 1 | 0.59 | 1.6193 | 120.6453 | 8.8963 | 2.4325 | 6.4638 | 11.1056 | 25 | 358 | 53 | 58843.19 | 4.26 | 245.57 | Note 3 | 11.11 | 10362.55 | 1587.31 | 12492.39 | VPC | 18.6158 | 49.4665 | 708.3607 | 33.3795 | 28.9457 | 4.4338 | Note 3 | 57.5994 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Albany | GA0950000 | Dougherty | 87260 | 4555.55 | Note 1 | Note 1 | 4895.2826 | 3949.34 | Note 1 | 40.98 | 158.38 | 4148.7 | 746.5826 | 101.1818 | 645.4008 | 945.9426 | 677.9 | 38622 | 55 | 8995947 | 5.31 | 214.71 | 189.9243 | 945.9426 | 533014.04 | 3427078.31 | 5018693.95 | CRUC | 7.1775 | 45.7828 | 2608.3809 | 102.5346 | 13.8008 | 88.7338 | 3.3982 | 61 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Alma | GA0050000 | Bacon | 4700 | 179.338 | Note 1 | Note 1 | 182.8114 | 146.418 | Note 1 | 13.2 | 16.321 | 175.939 | 6.8724 | 3.2538 | 3.6186 | 36.3934 | 48 | 1993 | 60 | 360659 | 5.27 | 191.36 | 12.234 | 36.39 | 17147.55 | 692.46 | 23489.15 | VPC | 4.4729 | 4.9744 | 206.5418 | 8.9513 | 8.6039 | 0.34745 | 0.29578 | 64.9451 | Level III (51-75) | Variable production cost (applied to Real Losses) | Unbilled metered | Total annual cost of operating water system
Americus | GA2610000 | Sumter | 14612 | 893.602 | Note 1 | Note 1 | 894.6757 | 607.4706 | Note 1 | 0.18527 | 1.5187 | 609.1745 | 285.5011 | 28.3563 | 257.1448 | 287.2051 | 143.9 | 7987 | 66 | 2070291.76 | 4.2666 | 250.5107 | 47.6151 | 287.2051 | 120955.45 | 64417.52 | 185799.82 | VPC | 9.7269 | 88.2066 | 4895.8044 | 23.2093 | 15.144 | 8.0653 | 5.4005 | 58 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI)
Ashburn | GA2870000 | Turner | 6789 | 227.827 | Note 1 | Note 1 | 284.7837 | 136.005 | Note 1 | 6.871 | 0.34001 | 143.216 | 141.5677 | 16.5551 | 125.0126 | 148.7788 | 45.12 | 2611 | 47.5 | 624555 | 2.66 | 387.91 | 11.0223 | 148.7788 | 42302.05 | 48493.64 | 93592.91 | VPC | 17.3713 | 131.1759 | 7590.875 | 34.7743 | 16.2015 | 18.5728 | 11.3418 | 45 | Tier II (26-50) | Billed Metered (BMAC) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI)
Athens-Clarke County Public Utilities Dept | GA0590000 | Clarke | 128000 | 4502.6 | Note 1 | Note 1 | 4438.2454 | 4012.72 | Note 1 | 77.59 | 10.0318 | 4100.3418 | 337.9036 | 61.3799 | 276.5238 | 425.5254 | 810.891 | 42899 | 93.17 | 7812855 | 5.96 | 338.01 | 368.0165 | 425.5254 | 361417.82 | 93467.8 | 484502.66 | VPC | 3.92 | 17.6601 | 934.2802 | 10.6036 | 8.4249 | 2.1788 | 0.75139 | 78 | Tier IV (71-90) | Customer Metering Inaccuracies (CMI) | Volume from Own Sources (VOS) | Billed Metered (BMAC)
Atlanta | GA1210001 | Fulton | 1200000 | 31323.507 | 5171.62 | 1425.905 | 35100.5999 | 24430.1 | 0.488 | Note 1 | 88.3 | 24518.888 | 10581.7119 | 1216.3335 | 9365.3784 | 10670.0119 | 2810.45 | 217437 | 103.57 | 146800885.75 | 7.4971 | 311.2424 | 1807.745 | 10670.0119 | 9118919.24 | 2914903.13 | 12061305.07 | VPC | 15.3259 | 118.0046 | 9129.702 | 55.3439 | 41.9382 | 13.4057 | 5.1807 | 79 | Tier IV (71-90) | Billed Unmetered (BUAC) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI)
Auburn | GA0130000 | Barrow | 7387 | Note 1 | 191.2079 | Note 1 | 189.3579 | 161.9024 | 6.98 | Note 1 | 2.367 | 171.2494 | 18.1086 | 1.0402 | 17.0684 | 20.4756 | 80.7 | 3072 | 52.1 | 2486240.53 | 15 | 550 | 17.0652 | 20.48 | 15603.23 | 9387.6 | 26292.67 | VPC | 0.9277 | 15.2222 | 579.4629 | 8.135 | 5.0792 | 3.0559 | 1.0002 | 81.2059 | Level IV (75-90) | Water imported | Billed unmetered | Unauthorized consumption
Augusta | GA2450000 | Richmond | 204000 | 13045.83 | Note 1 | Note 1 | 12333.1946 | 9092.7463 | Note 1 | 387.214 | 30 | 9509.9603 | 2823.2343 | 292.4976 | 2530.7368 | 3240.4483 | 1313.4 | 67512 | 81 | 49277217 | 6.35 | 240.03 | 509.4728 | 3240.45 | 1857359.53 | 607452.75 | 2564956.16 | VPC | 11.8699 | 102.7006 | 5279.0661 | 36.5092 | 27.5115 | 8.9977 | 4.9674 | 65.6764 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Billed metered
Austell | GA0670001 | Cobb | 7774 | Note 1 | 386.839 | Note 1 | 390.5492 | 277.034 | Note 1 | 3.8472 | 9.485 | 290.3662 | 100.183 | 4.2224 | 95.9607 | 113.5152 | 62.47 | 3919 | 128 | 2433508 | 7.79 | 3936.08 | 43.254 | 113.52 | 32742.37 | 377708.85 | 462927.83 | VPC | 2.9518 | 67.085 | 4208.5149 | 104.7337 | 8.3548 | 96.3789 | 2.2185 | 72 | Tier IV (71-90) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Unauthorized Consumption (UC)
Bainbridge | GA0870001 | Decatur | 13547 | 844.284 | Note 1 | Note 1 | 833.8607 | 571.052 | Note 1 | 52.612 | 10.4233 | 634.0873 | 199.7735 | 9.8119 | 189.9616 | 262.8087 | 170 | 5680 | 55 | 300000 | 3.05 | 355.33 | 35.5669 | 262.81 | 29926.35 | 67499.04 | 119823.71 | VPC | 4.7327 | 91.6272 | 3061.4273 | 17.1524 | 5.2687 | 11.8836 | 5.341 | 59.4626 | Level III (51-75) | Volume from own sources | Billed metered | Unbilled metered
Baldwin | GA1370001 | Habersham | 4774 | 664.185 | Note 1 | 458.697 | 200.2821 | 111.833 | Note 1 | 2.298 | 0.27958 | 114.4106 | 85.8715 | 2.5329 | 83.3385 | 88.4491 | 76 | 1836 | 103 | 2427147.87 | 0.17 | 1817.63 | 25.8112 | 88.4491 | 25428.13 | 151478.62 | 181591.84 | VPC | 3.7797 | 124.3599 | 3004.2731 | 96.3544 | 13.8497 | 82.5047 | 3.2288 | 66 | Tier III (51-70) | Water Exported (WE) | Customer Metering Inaccuracies (CMI) | Unauthorized Consumption (UC)
Baldwin County Water & Sewer | GA0090000 | Baldwin | 23067 | Note 1 | 698.565 | 12.547 | 685.8913 | 514.853 | Note 1 | 4.603 | 8.5736 | 528.0296 | 157.8616 | 19.0675 | 138.7941 | 171.0383 | 423 | 11343 | 60 | 4308088.22 | 8.37 | 1914.32 | 87.3784 | 171.04 | 159595.06 | 265696.34 | 450515.71 | VPC | 4.6055 | 33.5236 | 898.9547 | 37.4937 | 14.0699 | 23.4238 | 1.5884 | 69.3584 | Level III (51-75) | Billed metered | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Banks County | GA0110026 | Banks | 6453 | 224.52 | 15.213 | 15.198 | 229.274 | 196.173 | Note 1 | 22.624 | 2.8659 | 221.6629 | 7.6111 | 2.1631 | 5.448 | 33.101 | 334 | 3110 | 99 | 1401104 | 7.24 | 687.43 | 82.1508 | 33.1 | 15660.84 | 3745.1 | 36928.48 | VPC | 1.9056 | 4.7993 | 44.6885 | 6.2399 | 5.0356 | 1.2042 | 0.066317 | 64.0032 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Barnesville | GA1710000 | Lamar | 6755 | 667.24 | 2.876 | Note 1 | 670.116 | 347.0548 | Note 1 | 78.6097 | 0.86764 | 426.5321 | 243.5839 | 1.7353 | 241.8486 | 323.0612 | 81.4 | 4642 | 85 | 2151197 | 7.56 | 330.62 | 35.2653 | 323.0612 | 13118.67 | 79960 | 119355.46 | VPC | 1.0242 | 142.74 | 8140.0372 | 20.0514 | 2.8261 | 17.2253 | 6.858 | 72 | Tier IV (71-90) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Barrow County Water System / Barrow Co. BOC Transmission Mains | GA0130031 / GA0130034 | Barrow | 17066 | Note 1 | 709.492 | 243.439 | 462.2836 | 338.883 | 0.025 | 0.025 | 2.205 | 341.138 | 121.1456 | 5.3255 | 115.8201 | 123.3756 | 157.93 | 6564 | 109.48 | 3603121.24 | 12.99 | 639.67 | 73.4869 | 123.3756 | 69174.32 | 74086.67 | 144687.45 | VPC | 2.2228 | 48.3418 | 2009.2158 | 21.8253 | 10.5384 | 11.2868 | 1.5761 | 53 | Tier III (51-70) | Water Imported (WI) | Billed Metered (BMAC) | Customer Retail Unit Charge (CRUC)
Bartow County Water Department | GA0015001 | Bartow | 60650 | 193.576 | 2526.296 | 26.899 | 2737.0218 | 1758.183 | Note 1 | Note 1 | 34.306 | 1792.489 | 944.5328 | 35.5653 | 908.9675 | 978.8388 | 902.86 | 23741 | 122 | 22726125.26 | 8.7406 | 2876.5882 | 376.0836 | 978.8388 | 310862.94 | 2614725.2 | 3024272.37 | VPC | 4.1043 | 104.8954 | 2758.2592 | 123.2294 | 13.0939 | 110.1354 | 2.4169 | 57 | Tier III (51-70) | Water Imported (WI) | Variable Production Cost (VPC) | Billed Metered (BMAC)
Baxley | GA0010000 | Appling | 4741 | 248.711 | Note 1 | Note 1 | 248.1304 | 221.826 | Note 1 | 11.912 | 3.1016 | 236.8396 | 11.2907 | 8.4039 | 2.8868 | 26.3044 | 108.4 | 3340 | 58 | 475101.47 | 2.14 | 304.02 | 23.0212 | 26.23 | 17984.35 | 877.66 | 23426.45 | VPC | 6.8935 | 2.368 | 72.9627 | 5.6473 | 5.3845 | 0.26277 | 0.1254 | 75.25 | Level III (51-75) | Billed metered | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Blackshear | GA2290000 | Pierce | 5811 | 179.669 | Note 1 | Note 1 | 177.8901 | 151.787 | Note 1 | 0.18 | 2.2236 | 154.1906 | 23.6995 | 3.1019 | 20.5975 | 26.1031 | 36 | 2243 | 50 | 557517.08 | 5.02 | 258.21 | 9.6946 | 26.1 | 15571.76 | 5318.49 | 21510.89 | VPC | 3.7889 | 25.159 | 1567.5441 | 9.3135 | 6.9424 | 2.3712 | 2.1246 | 78.4143 | Level IV (75-90) | Customer retail unit cost (applied to Apparent Losses) | Volume from own sources | Unauthorized consumption
Blairsville | GA2910000 | Union | 5002 | 199.721 | Note 1 | Note 1 | 197.0607 | 125.508 | Note 1 | 1.078 | 0.31377 | 126.8998 | 70.1609 | 0.62754 | 69.5334 | 71.5527 | 74.6 | 1924 | 98 | 1093269 | 9.55 | 704.58 | 24.7595 | 71.5527 | 5993.01 | 48991.82 | 55965.44 | VPC | 0.8936 | 99.0137 | 2553.6513 | 28.5784 | 3.1149 | 25.4635 | 2.8084 | 73 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Customer Retail Unit Charge (CRUC)
Blakely | GA0990000 | Early | 7036 | 319.126 | Note 1 | Note 1 | 352.7813 | 172.949 | Note 1 | 3.947 | 0.43237 | 177.3284 | 175.453 | 14.6922 | 160.7608 | 179.8323 | 56 | 2706 | 53 | 223000 | 5.41 | 277.94 | 13.7129 | 179.8323 | 77901.4 | 44681.85 | 123800.46 | VPC | 14.8753 | 162.7644 | 7865.0084 | 45.3005 | 28.7884 | 16.5121 | 11.7233 | 80 | Tier IV (71-90) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
Blue Ridge Water & Sewer | GA1110000 | Fannin | 7200 | 332.218 | Note 1 | 13.252 | 324.0424 | 181.101 | Note 1 | 0.359 | 0.2 | 181.66 | 142.3824 | 2.7384 | 139.6439 | 142.9414 | 133 | 3494 | 110 | 2656801 | 8.38 | 688.17 | 49.9317 | 142.9414 | 22920.19 | 96098.76 | 119403.64 | VPC | 2.1473 | 109.498 | 2876.5873 | 34.0638 | 6.5599 | 27.5039 | 2.7967 | 84 | Tier IV (71-90) | Billed Metered (BMAC) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC)
Bowdon | GA0450000 | Carroll | 6180 | 169.013 | 8.542 | Note 1 | 182.7822 | 123.218 | Note 1 | 1.468 | 1.792 | 126.478 | 56.3042 | 1.8755 | 54.4287 | 59.5642 | 141 | 2377 | 77 | 1055420 | 6.09 | 789.19 | 31.4596 | 59.5642 | 11343.46 | 42954.56 | 56870.78 | VPC | 2.1617 | 62.7344 | 1057.586 | 22.8431 | 4.7722 | 18.0709 | 1.7301 | 74 | Tier IV (71-90) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
Braselton Water System | GA1570000 | Jackson | 12371 | 206.749 | 377.087 | 23.702 | 571.8096 | 496.916 | Note 1 | 0.452 | 1.2423 | 498.6103 | 73.1993 | 15.2376 | 57.9617 | 74.8936 | 133.95 | 6307 | 110 | 2311523.86 | 9.02 | 1919.73 | 67.0794 | 74.8936 | 137360.91 | 111270.83 | 251884.33 | VPC | 6.6191 | 25.1782 | 1185.5111 | 39.4216 | 21.7791 | 17.6424 | 0.86408 | 63 | Tier III (51-70) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Volume from Own Sources (VOS)
Bremen | GA1430000 | Haralson | 6200 | 102 | 288.676 | 84.609 | 309.7021 | 225.951 | Note 1 | 0.02 | 0.56488 | 226.5359 | 83.1662 | 1.1298 | 82.0365 | 83.7511 | 76 | 3105 | 90 | Note 5 | 5.97 | 3665.39 | 28.8065 | 83.7511 | 6744.64 | 300695.72 | 309584.16 | VPC | 0.99685 | 72.3857 | 2957.3355 | 99.0146 | 2.1722 | 96.8424 | 2.8478 | 75 | Tier IV (71-90) | Water Imported (WI) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Brunswick-Glynn Joint Water Sewer Commission | GA1270000 | Glynn | 37755 | 1917.736 | Note 1 | Note 1 | 1882.1631 | 1347.2651 | Note 1 | 217.352 | 23.527 | 1588.1441 | 294.019 | 144.1272 | 149.8918 | 534.898 | 238.5 | 18929 | 54 | 2672955.69 | 2.89 | 201.65 | 81.3951 | 534.9 | 416527.69 | 30225.68 | 495326.63 | VPC | 20.8605 | 21.6949 | 1721.855 | 23.6015 | 22.0047 | 1.5968 | 1.8415 | 63.8898 | Level III (51-75) | Volume from own sources | Billed metered | Customer metering inaccuracies
Brunswick-Glynn Joint Water Sewer Commission-St. Simons Island | GA1270001 | Glynn | 23579 | 967.086 | Note 1 | Note 1 | 987.427 | 795.1287 | Note 1 | 19.601 | 12.3428 | 827.0726 | 160.3544 | 85.0341 | 75.3204 | 192.2983 | 145.9 | 10833 | 56 | 1347932.16 | 2.89 | 201.65 | 49.3477 | 192.3 | 245748.42 | 15188.35 | 267378.24 | VPC | 21.5056 | 19.0489 | 1414.3739 | 24.0872 | 22.6852 | 1.402 | 1.5263 | 77.5957 | Level IV (75-90) | Billed metered | Customer metering inaccuracies | Volume from own sources
Buford | GA1350000 | Gwinnett | 8482 | 427.95 | 5.326 | Note 1 | 433.276 | 354.555 | 2.052 | 4.821 | 0.89152 | 362.3195 | 70.9565 | 23.4518 | 47.5046 | 76.669 | 81 | 3892 | 61 | 1901951.2 | 2.44 | 427.12 | 22.7551 | 76.67 | 56775.85 | 20290.18 | 79505.96 | VPC | 16.5086 | 33.4403 | 1606.7866 | 19.8011 | 14.5878 | 5.2133 | 2.0877 | 55 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Unmetered (BUAC) | Billed Metered (BMAC)
Butts County, et al. Water & Sewer Authority/Jackson/Jenkinsburg | GA0350051 | Butts | 24936 | 828.92 | 4.496 | 61.536 | 772.0605 | 472.736 | Note 1 | 7.463 | 1.1818 | 481.3808 | 290.6796 | 7.2237 | 283.456 | 299.3245 | 285 | 5935 | 75 | Note 5 | 6 | 548.1 | 66.5787 | 299.3245 | 42930.29 | 155362.21 | 203030.74 | VPC | 3.3346 | 130.8495 | 2724.883 | 33.4107 | 7.2334 | 26.1773 | 4.2575 | 64 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Number of Service Connections (Nc)
Byron | GA2250000 | Peach | 9486 | 269.134 | Note 1 | Note 1 | 266.4693 | 233.179 | Note 1 | 0.163 | 3.3309 | 236.6729 | 29.7964 | 8.4659 | 21.3306 | 33.2903 | 75.6 | 3427 | 60 | 625025 | 5 | 355.28 | 20.2147 | 33.29 | 42329.42 | 7578.32 | 51149.04 | VPC | 6.7681 | 17.0528 | 773.0143 | 14.5631 | 12.3517 | 2.2114 | 1.0552 | 51.3327 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Cairo | GA1310000 | Grady | 10000 | 516 | Note 1 | Note 1 | 498.5507 | 361 | Note 1 | Note 1 | 0.9025 | 361.9025 | 136.6482 | 5.4515 | 131.1968 | 137.5507 | 120 | 4502 | 70 | 430862 | 1.85 | 835 | 33.841 | 137.5507 | 10085.21 | 109549.29 | 120388.09 | VPC | 3.3175 | 79.8408 | 2995.3598 | 26.5736 | 2.2402 | 24.3335 | 3.8769 | 51 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Retail Unit Charge (CRUC) | Billed Metered (BMAC)
Calhoun | GA1290000 | Gordon | 58000 | 3738.764 | Note 1 | 1165.98 | 2675.8503 | 2072.135 | Note 1 | Note 1 | 5.1803 | 2077.3153 | 598.535 | 64.1465 | 534.3885 | 603.7153 | 863 | 22562 | 108 | 10955289.01 | 4.21 | 300.94 | 317.4544 | 603.7153 | 270056.64 | 160818.87 | 432434.49 | VPC | 7.7894 | 64.8913 | 1696.4983 | 19.0974 | 11.9695 | 7.1279 | 1.6834 | 71 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Water Exported (WE)
Camilla Water Department | GA2050001 | Mitchell | 5500 | 998.52 | Note 1 | Note 1 | 1023.1786 | 796.538 | Note 1 | Note 1 | 1.9913 | 798.5293 | 224.6493 | 45.9057 | 178.7435 | 226.6406 | 72 | 2891 | 55 | 1068032 | 2.2 | 123.91 | 16.5251 | 226.6406 | 100992.63 | 22148.11 | 123387.49 | VPC | 43.5037 | 169.3906 | 6801.5037 | 42.5945 | 34.9335 | 7.6611 | 10.8165 | 56 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI)
Canton | GA0570001 | Cherokee | 16375 | 1123.96 | 65.887 | 129.369 | 1059.1712 | 965.435 | Note 1 | 11.897 | 2.4136 | 979.7456 | 79.4257 | 24.7727 | 54.6529 | 93.7362 | 150 | 10300 | 80 | 5318567 | 6.81 | 645.89 | 68.8098 | 93.7362 | 167205.64 | 35299.78 | 211748.49 | VPC | 6.5894 | 14.5373 | 998.227 | 19.6607 | 16.2336 | 3.4272 | 0.79426 | 55 | Tier III (51-70) | Billed Metered (BMAC) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI)
Carroll County Water Authority | GA0450001 | Carroll | 48941 | 1823.781 | 1.269 | 463.227 | 1360.7024 | 1052.663 | Note 1 | 8.478 | 35.84 | 1096.981 | 263.7214 | 16.752 | 246.9694 | 308.0394 | 800.5 | 20280 | 97 | 7976448 | 8.04 | 398.09 | 261.0306 | 308.04 | 134686.16 | 98316.04 | 250644.75 | VPC | 2.2631 | 33.3643 | 845.2573 | 11.4893 | 6.6413 | 4.8479 | 0.94613 | 67.5694 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Carrollton | GA0450002 | Carroll | 25200 | 1713.29 | Note 1 | 0.355 | 1709.5153 | 1388.113 | Note 1 | 77.45 | 3.4703 | 1469.0333 | 240.482 | 6.9406 | 233.5414 | 321.4023 | 246 | 10086 | 80 | 3776923.91 | 6.21 | 462.41 | 83.0378 | 321.4023 | 43100.91 | 107991.88 | 188511.14 | VPC | 1.8853 | 63.4384 | 2600.9735 | 14.9804 | 4.2733 | 10.7071 | 2.8125 | 68 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Cartersville Water Department | GA0150002 | Bartow | 31135 | 4440.073 | Note 1 | 2237.206 | 2133.1937 | 1664.845 | Note 1 | Note 1 | 4.1621 | 1669.0071 | 464.1865 | 59.8143 | 404.3723 | 468.3487 | 235 | 11975 | 85 | 3607436.59 | 4.35 | 130.21 | 95.1723 | 468.3487 | 347826.25 | 52653.31 | 401021.51 | VPC | 13.6847 | 92.5152 | 4714.3371 | 33.443 | 29.046 | 4.3969 | 4.2488 | 59 | Tier III (51-70) | Volume from Own Sources (VOS) | Number of Service Connections (Nc) | Customer Metering Inaccuracies (CMI)
Catoosa Utility District Authority | GA0470000 | Catoosa | 52650 | 1352.573 | 552.022 | 54.84 | 1867.2973 | 1444.52 | Note 1 | Note 1 | 23.3412 | 1467.8612 | 399.436 | 22.8707 | 376.5654 | 422.7773 | 547 | 21351 | 113 | 6633299 | 4.12 | 207.71 | 254.1484 | 422.78 | 94227.1 | 78216.4 | 177291.7 | VPC | 2.9347 | 48.3203 | 1886.0804 | 8.0766 | 4.4132 | 3.6634 | 1.4817 | 70.514 | Level III (51-75) | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Cave Spring | GA1150000 | Floyd | 4180 | 275.924 | Note 1 | 92.087 | 183.744 | 78.938 | 0.024 | 2.753 | 2.2968 | 84.0118 | 99.7322 | 2.5371 | 97.1951 | 104.782 | 87 | 1677 | 107.5 | 859399 | 4.43 | 214.7 | 28.3381 | 104.78 | 11239.18 | 20867.8 | 33191.17 | VPC | 4.1448 | 158.7883 | 3060.7822 | 19.1455 | 6.702 | 12.4435 | 3.4298 | 76.2323 | Level IV (75-90) | Volume from own sources | Variable production cost (applied to Real Losses) | Water exported
Cedartown | GA2330000 | Polk | 9750 | 476.349 | Note 1 | Note 1 | 476.349 | 341.8333 | Note 1 | 50.834 | 0.85458 | 393.5218 | 82.8272 | 9.7228 | 73.1044 | 134.5157 | 85.9 | 4014 | 85 | Note 5 | 8.09 | 240.72 | 33.0981 | 134.5157 | 70514.26 | 17597.68 | 100554.41 | VPC | 6.6362 | 49.8968 | 2331.6175 | 21.9512 | 17.5671 | 4.3841 | 2.2087 | 68 | Tier III (51-70) | Customer Metering Inaccuracies (CMI) | Length of Mains (Lm) | Volume from Own Sources (VOS)
Centerville | GA1530000 | Houston | 11094 | 435.896 | 24.468 | Note 1 | 460.2768 | 297.201 | Note 1 | 12.828 | 5.7535 | 315.7825 | 144.4944 | 11.4822 | 133.0122 | 163.0758 | 48 | 4468 | 65 | 1931579.23 | 4.27 | 410.91 | 22.0614 | 163.08 | 49029.08 | 54656.03 | 111320.42 | VPC | 7.0408 | 81.5615 | 7592.0181 | 23.2062 | 10.9734 | 12.2328 | 6.0292 | 50.2633 | Level II (26-50) | Volume from own sources | Billed metered | Unbilled metered
Chatsworth Water Works Commission | GA2130000 | Murray | 30000 | 646.528 | 492.359 | 19.104 | 1119.973 | 789.93 | Note 1 | 15.332 | 1.9748 | 807.2368 | 312.7362 | 12.0836 | 300.6526 | 330.043 | 430 | 11922 | 90 | 5129500 | 7.3 | 731.75 | 135.1646 | 330.043 | 87193.13 | 220002.52 | 319859.93 | VPC | 2.7769 | 69.0912 | 1915.5946 | 25.7671 | 7.3136 | 18.4535 | 2.2243 | 71 | Tier IV (71-90) | Water Imported (WI) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI)
Chattooga CountY Water District 1 | GA0550000 | Chattoga | 7800 | 342.6894 | 9.7888 | 7.9395 | 362.542 | 183.8662 | Note 1 | Note 1 | 0.45967 | 184.3259 | 178.2161 | 10.5965 | 167.6196 | 178.6757 | 300 | 3460 | 90 | Note 5 | 6.29 | 302.19 | 70.3647 | 178.6757 | 66651.99 | 50652.96 | 117443.86 | VPC | 8.3906 | 132.7259 | 1530.7723 | 33.9032 | 19.2636 | 14.6396 | 2.3822 | 48 | Tier II (26-50) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Length of Mains (Lm)
Cherokee County Water & Sewerage Authority | GA0570002 | Cherokee | 210448 | 6529.4336 | 24.5994 | 458.855 | 6087.7697 | 5045.575 | Note 1 | 176.2638 | 0.116 | 5221.9548 | 865.8149 | 33.3722 | 832.4427 | 1042.1947 | 1333.29 | 75160 | 116.2 | 39423599 | 5.99 | 262.31 | 784.0933 | 1042.1947 | 196861.41 | 218358.05 | 461485.66 | VPC | 1.2165 | 30.3441 | 1710.5544 | 5.5245 | 2.6192 | 2.9052 | 1.0617 | 84 | Tier IV (71-90) | Volume from Own Sources (VOS) | Customer Retail Unit Charge (CRUC) | Unauthorized Consumption (UC)
Chickamauga | GA2950000 | Walker | 4150 | 304.252 | 3.053 | Note 1 | 323.3711 | 177.035 | Note 1 | 8 | 4.0421 | 189.0771 | 134.2939 | 5.0272 | 129.2667 | 146.3361 | 41.9 | 2005 | 145 | 590655.65 | 3.34 | 319.8 | 27.9142 | 146.34 | 16790.98 | 41339.49 | 61981.55 | VPC | 6.8695 | 176.6361 | 8452.3938 | 28.9928 | 8.3746 | 20.6182 | 4.6309 | 46.2745 | Level II (26-50) | Volume from own sources | Billed metered | Customer metering inaccuracies
Clarkesville | GA1370002 | Habersham | 5875 | 195.922 | 44.535 | 0 | 242.8859 | 145.365 | 12.475 | 11.369 | 0.3946 | 169.6036 | 73.2823 | 67.9609 | 5.3213 | 85.0459 | 61.5 | 2225 | 76.1 | 950568 | 6.12 | 366.37 | 18.5121 | 85.0459 | 387886.64 | 1949.58 | 394146.06 | VPC | 83.6828 | 6.5524 | 237.0573 | 175.2073 | 174.3311 | 0.87622 | 0.28745 | 59 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Unmetered (BUAC) | Water Imported (WI)
Claxton | GA1090001 | Evans | 1683 | 150.147 | 0 | 0 | 151.8938 | 99.103 | 0 | Note 1 | 0.24776 | 99.3508 | 52.543 | 1.4966 | 51.0465 | 52.7908 | 43 | 1797 | 60 | 1203800 | 4.74 | 310.77 | 10.9977 | 52.7908 | 7093.67 | 15863.71 | 23034.38 | VPC | 2.2817 | 77.826 | 3252.403 | 12.7754 | 3.9475 | 8.8279 | 4.6415 | 68 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Unauthorized Consumption (UC)
Clayton | GA2410000 | Rabun | 7225 | 0 | 401.046 | 12.703 | 386.5518 | 158.147 | 0 | 7.589 | 0.39537 | 166.1314 | 220.4204 | 6.8019 | 213.6185 | 228.4048 | 130 | 3593 | 160 | Note 5 | 13.32 | 3416.54 | 72.5474 | 228.4048 | 87875.2 | 729836.18 | 844990.28 | VPC | 5.1866 | 162.8879 | 4501.9707 | 227.5846 | 24.4573 | 203.1272 | 2.9445 | 57 | Tier III (51-70) | Water Imported (WI) | Billed Metered (BMAC) | Customer Retail Unit Charge (CRUC)
Clayton County Water Authority | GA0630000 | Clayton | 298374 | 9308.29 | 4.57 | 305.6719 | 9008.6378 | 7532.058 | 0.796 | 17.08 | 14.6 | 7564.534 | 1444.1038 | 23.861 | 1420.2428 | 1475.7838 | 1377.43 | 89947 | 100 | 32404933 | 4.06 | 443.47 | 764.454 | 1475.7838 | 96875 | 629835.05 | 740759.18 | VPC | 0.72679 | 43.2597 | 2824.8811 | 8.0793 | 1.077 | 7.0023 | 1.8579 | 73 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Unmetered (BUAC) | Customer Metering Inaccuracies (CMI)
Cleveland | GA3110000 | White | 4906 | 176.4145 | 95.6522 | 13.658 | 258.3013 | 189.4767 | 0 | 0.8856 | 0.47369 | 190.836 | 67.4653 | 5.8285 | 61.6368 | 68.8246 | 50 | 2369 | 90.7 | 1954858 | 3.07 | 1237.85 | 20.7191 | 68.8246 | 17851.79 | 76297.15 | 95831.55 | VPC | 6.7406 | 71.2824 | 3377.3606 | 39.7421 | 7.5356 | 32.2065 | 2.9749 | 65 | Tier III (51-70) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI) | Water Imported (WI)
Cobb County Water System / Cobb County-Marietta Water Authority | GA0670003 / GA0670002 | Cobb | 695000 | 29396.735 | Note 1 | 8322.417 | 21192.8095 | 19240 | Note 1 | Note 1 | 50.835 | 19290.835 | 1901.9745 | 158.9757 | 1742.9988 | 1952.8095 | 3248 | 195936 | 118 | 155402279.41 | 5.34 | 2183.18 | 2022.6568 | 1952.81 | 848930.26 | 3805280.15 | 4765192.37 | VPC | 2.2229 | 24.3719 | 1470.2399 | 23.7537 | 4.3327 | 19.421 | 0.86174 | 68.7861 | Level III (51-75) | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Cochran | GA0230000 | Bleckley | 5400 | 247.338 | 0 | 0 | 253.68 | 151.875 | 0.261 | 45.751 | 0.38034 | 198.2673 | 55.4127 | 0.76068 | 54.652 | 101.544 | 64 | 2761 | 53 | 1586032 | 7.18 | 394.13 | 14.7097 | 101.544 | 5461.68 | 21539.98 | 45183.41 | VPC | 0.75482 | 54.2309 | 2339.5539 | 9.7797 | 1.9782 | 7.8015 | 3.7154 | 57 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Unauthorized Consumption (UC)
College Park | GA1210002 | Fulton | 20382 | 45 | 1085 | Note 1 | 1140.2946 | 784 | 58 | 8 | 14.2537 | 864.2537 | 276.0409 | 6.7957 | 269.2452 | 298.2946 | 99.4 | 3102 | 69 | 5460661 | 7.51 | 4018 | 25.2619 | 298.29 | 51035.7 | 1081827.17 | 1222278.16 | VPC | 6.002 | 237.8008 | 7421.1072 | 365.204 | 16.4525 | 348.7515 | 10.6581 | 72.8592 | Level III (51-75) | Water imported | Unbilled metered | Unauthorized consumption
Columbia County Water Utility | GA0730000 | Columbia | 135000 | 6210.99 | 0 | 426.723 | 5784.2286 | 5146.783 | Note 1 | 147.2 | 16.18 | 5310.163 | 474.0656 | 37.4064 | 436.6592 | 637.4456 | 875.92 | 52771 | 50.61 | Note 5 | 3.74 | 443.68 | 233.7599 | 637.4456 | 138829.94 | 193736.97 | 405055.35 | VPC | 1.942 | 22.6702 | 1365.7944 | 6.3021 | 2.6308 | 3.6713 | 1.868 | 61 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Columbus Water Works | GA2150000 | Muscogee | 101967 | 10877.583 | 6.59 | 849.394 | 9982.9375 | 7267.129 | Note 1 | 1192.08 | 124.7867 | 8583.9957 | 1398.9417 | 269.8275 | 1129.1143 | 2715.8085 | 1199 | 72149 | 86.1 | 20493316.48 | 2.41 | 278.45 | 543.9594 | 2715.81 | 649272.31 | 314401.87 | 1330355.72 | VPC | 10.2462 | 42.876 | 2580.0365 | 13.3567 | 8.999 | 4.3577 | 2.0757 | 82.2527 | Level IV (75-90) | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Commerce | GA1570001 | Jackson | 6819 | 727.13 | 4.201 | 96.845 | 634.1946 | 302.194 | Note 1 | Note 1 | 7.9274 | 310.1214 | 324.0732 | 6.9429 | 317.1302 | 332.0006 | 126 | 4146 | 66 | 2060456 | 6.73 | 351.61 | 31.4028 | 332 | 46725.79 | 111506.17 | 161019.32 | VPC | 4.588 | 209.5634 | 6895.6349 | 38.165 | 11.2701 | 26.8949 | 10.0988 | 66.6882 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Coosa Water Authority | GA2910006 | Union | 5730 | 107.076 | 0 | 0 | 106.5433 | 76.421 | Note 1 | 0.34 | 0.19105 | 76.9521 | 29.5912 | 0.61308 | 28.9782 | 30.1223 | 170 | 3350 | 147 | 75827 | 4.39 | 708.66 | 76.3081 | 30.1223 | 2687.66 | 20535.66 | 23599.65 | VPC | 0.5014 | 23.6992 | 467.0129 | 6.9323 | 0.80229 | 6.13 | 0.37975 | 59 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Cordele | GA0810001 | Crisp | 12000 | 661.864 | 0 | 0 | 661.864 | 519.223 | 0 | 10.608 | 1.2981 | 531.1291 | 130.7349 | 2.5961 | 128.1388 | 142.641 | 133 | 6302 | 70 | Note 5 | 3.47 | 223.72 | 42.5364 | 142.641 | 9008.52 | 28667.22 | 40339.36 | VPC | 1.1286 | 55.707 | 2639.5886 | 5.9784 | 1.4295 | 4.5489 | 3.0125 | 70 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Cornelia | GA1370003 | Habersham | 6130 | 1025.19 | Note 1 | 5.113 | 1062.7932 | 926.193 | Note 1 | 13.632 | 13.2849 | 953.1099 | 109.6833 | 11.9087 | 97.7747 | 136.6002 | 66.3 | 2883 | 91 | 2773957.7 | 4.28 | 375.49 | 26.2775 | 136.6 | 50969.08 | 36713.41 | 97789.52 | VPC | 11.3168 | 92.9156 | 4040.3591 | 30.4136 | 17.6792 | 12.7344 | 3.7209 | 76.9655 | Level IV (75-90) | Volume from own sources | Billed metered | Unbilled metered
Covington | GA2170001 | Newton | 17272 | 0 | 2202.376 | 1076.579 | 1125.797 | 962.09 | 0 | 0 | 2.4052 | 964.4952 | 161.3018 | 4.8105 | 156.4913 | 163.707 | 185 | 9203 | 90.7 | 5894998.63 | 6.13 | 2240 | 78.8341 | 163.707 | 29488.06 | 350540.57 | 385416.33 | VPC | 1.4321 | 46.5873 | 2317.5317 | 41.294 | 3.2042 | 38.0898 | 1.9851 | 64 | Tier III (51-70) | Water Imported (WI) | Water Exported (WE) | Customer Metering Inaccuracies (CMI)
Coweta County Water & Sewerage Authority | GA0770042 | Coweta | 90000 | 1887.7917 | 1203.276 | 285.271 | 2823.7398 | 2387.905 | 0 | 2.844 | 38.398 | 2429.147 | 394.5928 | 5.0264 | 389.5664 | 435.8348 | 1112 | 34411 | 115 | Note 5 | 6.5 | 2837.03 | 469.1785 | 435.8348 | 32701.73 | 1105211.57 | 1254918.09 | VPC | 0.40019 | 31.0164 | 959.8068 | 33.0683 | 0.95033 | 32.118 | 0.83032 | 74 | Tier IV (71-90) | Volume from Own Sources (VOS) | Water Imported (WI) | Customer Retail Unit Charge (CRUC)
Cumming Utilities - City of Cumming, GA | GA1170000 | Forsyth | 66957 | 3202.558 | 0.0888 | 447.8309 | 2747.9146 | 2171.8011 | 0 | 19.2666 | 4.6088 | 2195.6765 | 552.2381 | 28.5289 | 523.7092 | 576.1134 | 394 | 22287 | 118.5 | Note 5 | 2.91 | 482.01 | 236.7897 | 576.1134 | 82641.87 | 252433.06 | 346583.08 | VPC | 3.507 | 64.3792 | 3641.6743 | 15.0345 | 3.7081 | 11.3265 | 2.2117 | 72 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Number of Service Connections (Nc)
Cuthbert | GA2430000 | Randolph | 3770 | 204.4 | Note 1 | Note 1 | 204.4 | 105.063 | Note 1 | Note 1 | 2.555 | 107.618 | 96.782 | 11.1645 | 85.6175 | 99.337 | 50 | 1382 | 56 | 361887 | 3.9 | 383.67 | Note 3 | 99.34 | 43541.56 | 32848.86 | 77370.7 | VPC | 22.1329 | 169.7312 | 4691.3697 | 55.2753 | 31.5062 | 23.7691 | Note 3 | 37.3667 | Level II (26-50) | Volume from own sources | Billed metered | Customer metering inaccuracies
Dade County Water & Swwer Authority | GA0830000 | Dade | 16251 | 736.327 | 0 | 0 | 751.3541 | 456.445 | Note 1 | Note 1 | 8.651 | 465.096 | 286.2581 | 52.9983 | 233.2597 | 294.9091 | 364 | 8461 | 104 | Note 5 | 4.92 | 702.6 | 122.9293 | 294.9091 | 260751.81 | 163888.3 | 430718.3 | VPC | 17.1612 | 75.531 | 1755.6808 | 50.1879 | 30.8181 | 19.3698 | 1.8975 | 72 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Dahlonega / Dahlonega Water System | GA1870000 | Lumpkin | 7500 | 357.225 | 0 | 40.006 | 309.5354 | 226.773 | 0 | 0 | 0.56693 | 227.3399 | 82.1955 | 3.4245 | 78.771 | 82.7624 | 70.1 | 2525 | 150 | 2291812 | 11.27 | 599.87 | 41.5 | 82.7624 | 38594.13 | 47252.34 | 86186.56 | VPC | 3.7157 | 85.4697 | 3078.6147 | 33.9986 | 15.2848 | 18.7138 | 1.8981 | 67 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Customer Retail Unit Charge (CRUC)
Dallas | GA2230000 | Paulding | 14000 | 11.458 | 277.097 | 0 | 288.3292 | 203.008 | 0 | 1 | 0.50752 | 204.5155 | 83.8137 | 3.0757 | 80.738 | 85.3212 | 43.53 | 3808 | 81.04 | Note 5 | 9.7 | 4548 | 23.8618 | 85.3212 | 29782.51 | 367196.43 | 403835.14 | VPC | 2.2129 | 58.0882 | 5081.553 | 104.2487 | 7.821 | 96.4276 | 3.3836 | 85 | Tier IV (71-90) | Water Imported (WI) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
Dalton Utilities | GA3130000 | Whitfield | 102864 | 9062.483 | 200.8 | 166.92 | 8876.4201 | 5879.02 | 73.867 | 0 | 237.99 | 6190.877 | 2685.5431 | 53.375 | 2632.1682 | 2923.5331 | 1215.05 | 38503 | 110.4 | 21939000 | 4.4834 | 242.81 | 497.6101 | 2923.5331 | 239301.14 | 639116.75 | 936204.24 | VPC | 3.798 | 187.295 | 5935.0805 | 22.8143 | 6.2151 | 16.5991 | 5.2896 | 76 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Dawson | GA2730001 | Terrell | 5258 | 467.854 | 0 | 0 | 584.8175 | 156.831 | 0 | 0 | 0.39208 | 157.2231 | 427.5944 | 22.1702 | 405.4242 | 427.9865 | 50 | 2030 | 50 | 912120 | 3.92 | 275.3 | 10.4938 | 427.9865 | 86907.19 | 111613.29 | 198628.41 | VPC | 29.9213 | 547.1681 | 22215.0259 | 97.7933 | 42.8114 | 54.9819 | 38.6348 | 50 | Tier II (26-50) | Volume from Own Sources (VOS) | Length of Mains (Lm) | Billed Metered (BMAC)
DeKalb County Department of Watershed Management | GA0890001 | DeKalb | 750000 | 23952.41 | 0 | 6.558 | 23945.852 | 23000 | 0 | 5.67 | 57.5 | 23063.17 | 882.682 | 115 | 767.682 | 945.852 | 3081 | 200424 | 104 | Note 5 | 1.4 | 236.72 | 1773.9395 | 945.852 | 161000 | 181725.68 | 357679.29 | VPC | 1.572 | 10.4939 | 682.648 | 1.71 | 0.8033 | 0.90671 | 0.43276 | 66 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Customer Retail Unit Charge (CRUC)
Demorest | GA1370004 | Habersham | 16500 | 130.285 | 550.636 | 45.72 | 635.201 | 502.839 | 0 | 2.908 | 1.2571 | 507.0041 | 128.1969 | 7.6228 | 120.5742 | 132.362 | 310 | 7242 | 110 | Note 5 | 4.01 | 1953.44 | 110.9505 | 132.362 | 30506.82 | 235534.37 | 274177.46 | VPC | 2.8838 | 45.6145 | 1065.6134 | 36.7359 | 4.2125 | 32.5234 | 1.0867 | 53 | Tier III (51-70) | Water Imported (WI) | Volume from Own Sources (VOS) | Variable Production Cost (VPC)
Douglas | GA0690002 | Coffee | 11255 | 1290.705 | Note 1 | Note 1 | 1277.9257 | 1075.075 | Note 1 | Note 1 | 15.9741 | 1091.0491 | 186.8767 | 62.4654 | 124.4113 | 202.8507 | 125 | 6818 | 65 | 4175263.75 | 4.09 | 225.01 | 40.3076 | 202.85 | 255483.47 | 27993.78 | 287071.58 | VPC | 25.1009 | 49.9931 | 2726.8224 | 41.5778 | 37.4719 | 4.1059 | 3.0865 | 62.3529 | Level III (51-75) | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered
Douglas/Oak Park | GA0690014 | Coffee | 260 | 58.263 | Note 1 | Note 1 | 57.6861 | 47.916 | Note 1 | Note 1 | 0.72108 | 48.6371 | 9.0491 | 2.7859 | 6.2632 | 9.7701 | 12 | 798 | 65 | 75285 | 4.09 | 404.18 | Note 3 | 9.77 | 11394.33 | 2531.44 | 14217.21 | VPC | 9.5647 | 21.5029 | 1429.9456 | 17.4508 | 14.2786 | 3.1722 | Note 3 | 62.3529 | Level III (51-75) | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered
Douglsville-Douglas County Water and Sewer Authority | GA0970000 | Douglas | 144237 | 4235.3428 | 0.36835 | 0.90703 | 4252.0605 | 3707.725 | 0 | 4.7216 | 16.291 | 3728.7376 | 523.3228 | 75.0733 | 448.2495 | 544.3355 | 951 | 45522 | 99 | 19466311 | 5.61 | 332.38 | 432.6519 | 544.3355 | 420781.99 | 148989.17 | 576755.33 | VPC | 4.5183 | 26.9777 | 1291.3573 | 12.5164 | 9.2435 | 3.2729 | 1.0361 | 81 | Tier IV (71-90) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
Dublin | GA1750002 | Laurens | 19565 | 1046.12 | 0 | 0 | 1046.12 | 725.205 | Note 1 | 30.345 | 1.813 | 757.363 | 288.757 | 60.4954 | 228.2616 | 320.915 | 230 | 7525 | 62 | 2616628 | 5.47 | 348.12 | 53.7021 | 320.915 | 319211.19 | 79462.43 | 409868.47 | VPC | 22.0254 | 83.1062 | 2719.0186 | 52.9799 | 42.4201 | 10.5598 | 4.2505 | 54 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Variable Production Cost (VPC)
East Dublin | GA1750004 | Laurens | 4087 | 137.762 | 0 | 0 | 137.762 | 112.307 | 0 | 12 | 0.28077 | 124.5878 | 13.1742 | 3.0984 | 10.0758 | 25.455 | 40 | 1382 | 65 | 918000 | 3.52 | 493 | 10.0523 | 25.455 | 10165.11 | 4967.38 | 21186.9 | VPC | 6.1424 | 19.9747 | 690.1247 | 10.9497 | 7.3554 | 3.5943 | 1.0023 | 65 | Tier III (51-70) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
East Point Water Treatment Plant | GA1210003 | Fulton | 33712 | 2203.14 | Note 1 | 1340.852 | 858.3365 | 300.159 | Note 1 | Note 1 | 10.7292 | 310.8882 | 547.4483 | 4.4046 | 543.0437 | 558.1775 | 177 | 10533 | 89 | 17447400 | 3.91 | 330 | 82.4313 | 558.18 | 17221.89 | 2123300.86 | 2144063.39 | CRUC | 1.1457 | 141.2504 | 8405.5986 | 203.2206 | 1.635 | 201.5856 | 6.5878 | 72.0053 | Level III (51-75) | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | Volume from own sources
Eastman | GA0910002 | Dodge | 7833 | 423.295 | Note 1 | Note 1 | 408.9807 | 235.077 | Note 1 | 14.386 | 5.1123 | 254.5753 | 154.4054 | 2.2354 | 152.1701 | 173.9037 | 64.8 | 3506 | 67 | 1824227 | 3.3 | 285.79 | 21.434 | 173.9 | 7376.7 | 502161.18 | 515110.29 | CRUC | 1.7468 | 118.9117 | 6433.7076 | 145.3331 | 2.104 | 143.2291 | 7.0995 | 60.4783 | Level III (51-75) | Volume from own sources | Billed metered | Customer metering inaccuracies
Eatonton-Putnam Water & Sewer Authority | GA2370000 | Putnam | 11479 | 0 | 403.717 | 9.098 | 394.619 | 362.564 | 0 | 21.054 | 1e-06 | 383.618 | 11.001 | 9.6418 | 1.3592 | 32.055 | 241 | 14256 | 78 | 2167084 | 3.5 | 418.66 | 97.9997 | 32.055 | 32422.19 | 569.06 | 41805.71 | VPC | 1.853 | 0.26122 | 15.4521 | 2.3142 | 2.2743 | 0.039917 | 0.01387 | 81 | Tier IV (71-90) | Billed Metered (BMAC) | Water Imported (WI) | Unauthorized Consumption (UC)
Effingham County Surface Water System | GA1030131 | Effingham | 9869 | Note 1 | 947.774 | Note 1 | 947.774 | 913.223 | Note 1 | Note 1 | 0.01 | 913.233 | 34.541 | 13.877 | 20.664 | 34.551 | 93.83 | 3735 | 45 | 1791000 | 2.92 | 1889.24 | 17.5398 | 34.55 | 40520.74 | 39039.32 | 79578.95 | VPC | 10.1791 | 15.1576 | 603.3655 | 21.3012 | 10.8489 | 10.4523 | 1.1781 | 55.0222 | Level III (51-75) | Water imported | Billed metered | Total annual cost of operating water system
Elberton | GA1050001 | Elbert | 9000 | 610.947 | Note 1 | 138.099 | 476.9922 | 405.861 | 0.342 | 5.69 | 1.0155 | 412.9085 | 64.0837 | -4.596 | 68.6797 | 70.7892 | 128.1 | 3962 | 74 | 1580549 | 3.88 | 561.42 | 34.7705 | 70.7892 | 33289.04 | 38558.15 | 75611.8 | VPC | -3.1781 | 47.4921 | 1468.88 | 18.1341 | 8.4021 | 9.732 | 1.9752 | 62 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Water Exported (WE)
Ellijay Gilmer County Water & Sewer Authority | GA1230000 | Gilmer | 15485 | 975 | 0 | 38 | 937.4963 | 774 | 0 | 43 | 1.935 | 818.935 | 118.5613 | 9.2152 | 109.346 | 163.4963 | 243 | 6666 | 93.8 | 2525786.71 | 4.73 | 515.16 | 79.2426 | 163.4963 | 42402.35 | 56330.69 | 121881.76 | VPC | 3.7875 | 44.9412 | 1232.8318 | 14.8114 | 6.361 | 8.4504 | 1.3799 | 83 | Tier IV (71-90) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
Etowah Water & Sewer Authority | GA0850007 | Dawson | 13843 | 592.85 | 1.18 | 0 | 600.0727 | 451.146 | 0 | 2.378 | 32.811 | 486.335 | 113.7377 | 10.5035 | 103.2342 | 148.9267 | 205.22 | 6912 | 99 | 3745301.1 | 13.86 | 350.15 | 77.5833 | 148.9267 | 144922.27 | 36147.47 | 193391.17 | VPC | 4.1633 | 40.9192 | 1378.1967 | 26.1964 | 20.9668 | 5.2297 | 1.3306 | 76 | Tier IV (71-90) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Variable Production Cost (VPC)
Fairburn | GA1210004 | Fulton | 14000 | Note 1 | 495.778 | Note 1 | 500.7859 | 244.354 | Note 1 | Note 1 | 6.2598 | 250.6138 | 250.172 | 4.3311 | 245.841 | 256.4319 | 75.1 | 6221 | 75 | 3312765 | 8.32 | 4950 | 36.6672 | 256.43 | 36034.52 | 1216912.77 | 1283933.42 | VPC | 1.9074 | 108.2683 | 8968.5338 | 201.4061 | 5.7924 | 195.6137 | 6.7047 | 73.5418 | Level III (51-75) | Water imported | Customer metering inaccuracies | Unauthorized consumption
Fayette County Water System | GA1130001 | Fayette | 77051 | 3436.319 | 19.6492 | 363.2475 | 3089.4711 | 2849.8914 | 0.7482 | 0.75925 | 7.6266 | 2859.0255 | 230.4456 | 72.4297 | 158.0159 | 238.8315 | 654 | 36315 | 87.7188 | 15065704 | 6.3562 | 530.5231 | 287.6883 | 238.8315 | 460287.86 | 83831.08 | 548567.84 | VPC | 5.4643 | 11.9213 | 661.9576 | 14.9833 | 12.6749 | 2.3084 | 0.54926 | 76 | Tier IV (71-90) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Fayettville | GA1130003 | Fayettville | 18645 | 294.309 | 359.8032 | Note 1 | 656.2466 | 461.4346 | Note 1 | Note 1 | 1.1536 | 462.5882 | 193.6585 | 6.9681 | 186.6903 | 194.812 | 100 | 7842 | 60 | Note 5 | 3.87 | 1463.59 | 37.6089 | 194.812 | 26966.66 | 273238.1 | 301893.13 | VPC | 2.4344 | 65.2232 | 5114.8036 | 38.2817 | 3.4387 | 34.8429 | 4.964 | 67 | Tier III (51-70) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Number of Service Connections (Nc)
Fitzgerald Utilities | GA0170000 | Ben Hill | 14011 | 770.6403 | Note 1 | Note 1 | 748.1945 | 675.082 | Note 1 | 10.407 | 9.3524 | 694.8414 | 53.353 | 14.0678 | 39.2853 | 73.1125 | 132 | 6055 | 61.9 | 1123686 | 2.96 | 142.76 | 36.655 | 73.11 | 41640.6 | 5608.36 | 50069.82 | VPC | 6.3653 | 17.7755 | 815.3853 | 7.8033 | 6.8771 | 0.92624 | 1.0718 | 57.7569 | Level III (51-75) | Volume from own sources | Unbilled metered | Billed metered
Flowery Branch | GA1390000 | Towns | 4254 | 115.229 | 0.887 | Note 1 | 114.4 | 102.303 | Note 1 | 1.6 | 1.43 | 105.333 | 9.067 | 3.7553 | 5.3117 | 12.097 | 19.9 | 7505 | 80 | 898673.41 | 6.74 | 956.18 | 36.0155 | 12.1 | 25310.4 | 5078.99 | 33286.62 | VPC | 1.3709 | 1.9391 | 731.2931 | 4.0492 | 3.3725 | 0.67675 | 0.14748 | 56.8682 | Level III (51-75) | Volume from own sources | Unbilled metered | Unauthorized consumption
Floyd County | GA1150001 | Floyd | 99566 | 1399.116 | 623.483 | 59 | 2003.6724 | 1408.295 | 0 | 14.6 | 1 | 1423.895 | 579.7774 | 81.9307 | 497.8468 | 595.3774 | 591 | 19084 | 90 | 5977702 | 4.97 | 540.71 | 199.068 | 595.3774 | 403791.95 | 269190.72 | 681417.75 | VPC | 11.7621 | 71.4716 | 2307.8913 | 35.2642 | 21.1587 | 14.1056 | 2.5009 | 75 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Water Imported (WI)
Folkston | GA0490000 | Charlton | 3300 | 168.823 | 0 | 2.056 | 164.5795 | 145.854 | 0 | 0.188 | 0.36464 | 146.4066 | 18.1729 | 2.2044 | 15.9684 | 18.7255 | 61.2 | 2412 | 52 | 432348.7 | 3.02 | 390.48 | 13.1511 | 18.7255 | 6652.42 | 6235.35 | 13103.57 | VPC | 2.504 | 18.1381 | 714.8552 | 5.3432 | 2.7581 | 2.5851 | 1.2142 | 48 | Tier II (26-50) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Length of Mains (Lm)
Forsyth County Department of Water and Sewer | GA1170050 | Forsyth | 198732 | 4781.446 | 370.081 | 50.016 | 5372.933 | 4802.576 | 0 | 11.998 | 12.0064 | 4826.5804 | 546.3526 | 122.2695 | 424.0831 | 570.357 | 1108.2 | 66105 | 116.6 | 40228158 | 0.61 | 1349.82 | 677.161 | 570.357 | 1295011.89 | 572435.8 | 1899849.36 | VPC | 5.0675 | 17.5762 | 1048.4311 | 28.2497 | 19.5902 | 8.6595 | 0.62627 | 72 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Forsyth/Water Department | GA2070001 | Monroe | 7400 | 492.33 | 6.644 | 16.576 | 508.2729 | 483.04 | Note 1 | Note 1 | 2.1 | 485.14 | 23.1329 | 4.9056 | 18.2273 | 25.2329 | 50 | 3302 | 70 | 1697456.26 | 6.89 | 551.8 | 19.5662 | 25.23 | 33799.71 | 10057.8 | 45016.29 | VPC | 4.0703 | 15.1235 | 998.7538 | 13.2821 | 10.2361 | 3.046 | 0.93157 | 74.7089 | Level III (51-75) | Variable production cost (applied to Real Losses) | Billed metered | Volume from own sources
Fort Oglethorpe | GA0470001 | Catoosa | 7909 | Note 1 | 290.599 | Note 1 | 290.599 | 111.124 | Note 1 | Note 1 | 3.6325 | 114.7565 | 175.8425 | 1.0043 | 174.8382 | 179.475 | 38 | 3107 | 110 | 1413462 | 8.06 | 2.34 | 26.9659 | 179.48 | 8094.72 | 409.12 | 8512.34 | VPC | 0.88559 | 154.1708 | 12605.4942 | 2.737 | 2.6053 | 0.13168 | 6.4837 | 79.9222 | Level IV (75-90) | Billed metered | Customer metering inaccuracies | Unauthorized consumption
Fort Valley Utility Commission | GA2250001 | Peach | 11855 | 582.403 | Note 1 | Note 1 | 588.2859 | 455.776 | Note 1 | Note 1 | 7.3536 | 463.1296 | 125.1563 | 16.7063 | 108.45 | 132.5099 | 156 | 5514 | 55 | 2733339 | 6 | 405.28 | 33.5465 | 132.51 | 100275.62 | 43952.6 | 147208.48 | VPC | 8.3008 | 53.8852 | 1904.6359 | 26.1567 | 18.1856 | 7.9711 | 3.2328 | 62.8529 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Franklin County | GA1190051 | Flanklin | 6864 | 428.2635 | 302.7591 | 118.9527 | 619.7282 | 431.5705 | 0 | 6.0816 | 1.0789 | 438.731 | 180.9972 | 15.6935 | 165.3037 | 188.1577 | 244 | 2344 | 125 | 2511220 | 5.84 | 2014.16 | 76.2686 | 188.1577 | 90930.34 | 332948.16 | 438300.9 | VPC | 18.3429 | 193.2111 | 1856.094 | 180.8355 | 38.7928 | 142.0427 | 2.1674 | 58 | Tier III (51-70) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Variable Production Cost (VPC)
Gainesville-Department of Water Resources | GA1390001 | Hall | 140000 | 7046 | Note 1 | Note 1 | 7038.841 | 6348 | Note 1 | 33.369 | 126.585 | 6507.954 | 530.887 | 217.3332 | 313.5538 | 690.841 | 1443 | 60949 | 129 | 33047730 | 6.06 | 434 | 798.0427 | 690.841 | 1311173.21 | 136082.34 | 1516675.59 | VPC | 9.7694 | 14.0946 | 595.3233 | 23.7454 | 21.5126 | 2.2327 | 0.3929 | 76 | Tier IV (71-90) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Customer Metering Inaccuracies (CMI)
Garden City | GA0510000 | Chatham | 9331 | 344.249 | Note 1 | Note 1 | 332.49 | 251.737 | Note 1 | 13.65 | 0.884 | 266.271 | 66.219 | 6.6747 | 59.5443 | 80.753 | 51 | 3589 | 60 | Note 5 | 2.55 | 204.58 | 17.8323 | 80.753 | 16367.24 | 12181.56 | 31522.17 | VPC | 5.0953 | 45.4541 | 3198.7244 | 7.9545 | 4.5604 | 3.3941 | 3.3391 | 48 | Tier II (26-50) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Variable Production Cost (VPC)
Glen of Robin Hood | GA0510109 | Chatham | 6000 | 190.313 | Note 1 | Note 1 | 190.313 | 180.839 | Note 1 | Note 1 | 0.4521 | 181.2911 | 9.0219 | 0.90419 | 8.1177 | 9.474 | 37 | 3140 | 45 | Note 5 | 2.75 | 262.73 | 11.024 | 9.474 | 2486.54 | 2132.77 | 4738.08 | VPC | 0.78893 | 7.0829 | 601.089 | 1.4711 | 0.79189 | 0.67922 | 0.73637 | 51 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Glennville | GA2670002 | Tattnal | 5300 | 258.13 | 0 | 0 | 258.13 | 218.534 | 0 | 8.089 | 0.54634 | 227.1693 | 30.9607 | 1.6606 | 29.3 | 39.596 | 52 | 2121 | 46.8 | 634236.36 | 4.36 | 250.01 | 10.2401 | 39.596 | 7157.1 | 7325.3 | 16641.32 | VPC | 2.1451 | 37.8473 | 1543.7312 | 6.8281 | 3.3744 | 3.4537 | 2.8613 | 61 | Tier III (51-70) | Volume from Own Sources (VOS) | Length of Mains (Lm) | Unauthorized Consumption (UC)
Gray | GA1690000 | Jones | 9191 | 107.536 | 107.285 | 7.838 | 207.4149 | 167.631 | 0 | 2.2363 | 0.41908 | 170.2863 | 37.1285 | 4.3048 | 32.8237 | 39.7839 | 60.6 | 1998 | 60 | 966326.62 | 7.02 | 2250.51 | 13.7433 | 39.7839 | 30002.26 | 73870.04 | 109848.19 | VPC | 5.9029 | 45.009 | 1483.959 | 51.9881 | 15.0161 | 36.972 | 2.3883 | 50 | Tier II (26-50) | Water Imported (WI) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI)
Griffin | GA2550000 | Spalding | 100000 | 2887.76 | Note 1 | 1870.7635 | 933.0215 | 740.3252 | Note 1 | 36.169 | 7.5229 | 784.0171 | 149.0044 | 11.4658 | 137.5386 | 192.6963 | 208.84 | 11681 | 77.6 | 9515979.56 | 8.84 | 441.35 | 81.629 | 192.6963 | 98320.13 | 60702.66 | 178306.22 | VPC | 2.6892 | 32.2591 | 1804.3385 | 13.6138 | 8.4171 | 5.1967 | 1.6849 | 82 | Tier IV (71-90) | Water Exported (WE) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Grovetown | GA0730001 | Columbia | 14053 | 12.5396 | 367.9941 | 0 | 382.822 | 337.0686 | 0 | 0.055527 | 0.84267 | 337.9668 | 44.8552 | 1.6853 | 43.1699 | 45.7534 | 69.18 | 5475 | 80 | 3148171.76 | 6.8569 | 1890.5718 | 34.909 | 45.7534 | 11556.28 | 81615.7 | 94870.09 | VPC | 0.84336 | 21.6025 | 1709.6497 | 17.0177 | 2.1107 | 14.907 | 1.2366 | 49 | Tier II (26-50) | Water Imported (WI) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI)
Gwinnett County Department of Water Resources / Lawrenceville | GA135004 / GA1350005 | Gwinnett | 973807 | 27676.63 | 0 | 118.304 | 27506.1832 | 24191.757 | 0 | 1.868 | 9.536 | 24203.161 | 3303.0222 | 447.3779 | 2855.6443 | 3314.4262 | 3989.9 | 281032 | 117 | 22889132 | 5.84 | 326.65 | 2722.0235 | 3314.4262 | 2612522.73 | 932796.21 | 3549044.06 | VPC | 4.3614 | 27.8391 | 1960.872 | 12.6154 | 9.2962 | 3.3192 | 1.0491 | 84 | Tier IV (71-90) | Volume from Own Sources (VOS) | Systematic Data Handling Errors (SDHE) | Unauthorized Consumption (UC)
Hahira | GA1850000 | Lowndes | 3562 | 92.09 | Note 1 | Note 1 | 96.9368 | 86.25 | Note 1 | 2.113 | 1.2117 | 89.5747 | 7.3621 | 1.8036 | 5.5585 | 10.6868 | 25 | 2961 | 60 | 391941.43 | 6.13 | 1216.75 | 12.6889 | 10.69 | 11050.64 | 6763.35 | 21859.33 | VPC | 1.6688 | 5.1431 | 609.1545 | 6.0162 | 3.7321 | 2.2841 | 0.43806 | 59.9706 | Level III (51-75) | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Hampton GA | GA1510000 | Henry | 7305 | 35.41 | 187.4836 | 0 | 224.1576 | 156.2409 | 0 | 0 | 1.586 | 157.8269 | 66.3307 | 9.0044 | 57.3263 | 67.9167 | 41.1 | 2576 | 54 | 1249875 | 14.82 | 3291.07 | 11.9985 | 67.9167 | 133445.34 | 188665 | 327329.98 | VPC | 9.5767 | 60.9699 | 3821.3739 | 125.0428 | 51.8033 | 73.2395 | 4.7778 | 59 | Tier III (51-70) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Hapeville Water Department | GA1210006 | Fulton | 6000 | 0 | 291.459 | 0 | 289.6631 | 208.372 | Note 1 | 1.25 | 0.52093 | 210.1429 | 79.5202 | 5.3199 | 74.2003 | 81.2911 | 41 | 2503 | 81.6 | 1417491.15 | 8.78 | 4863.43 | 17.7888 | 81.2911 | 46608.46 | 360867.96 | 416089.21 | VPC | 5.823 | 81.2179 | 4958.2559 | 162.7952 | 18.621 | 144.1742 | 4.1712 | 65 | Tier III (51-70) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Unauthorized Consumption (UC)
Haralson County Water Authority | GA1430007 | Haralson | 11000 | 808.837 | 73.361 | 506.63 | 383.2327 | 252.685 | Note 1 | 16.971 | 0.63171 | 270.2877 | 112.9449 | 1.3174 | 111.6276 | 130.5477 | 395 | 5926 | 89.6 | 3283000 | 6.26 | 386.14 | 98.9574 | 130.5477 | 8226.78 | 43103.87 | 58127.76 | VPC | 0.60905 | 51.608 | 774.2506 | 8.6619 | 1.3883 | 7.2737 | 1.128 | 67 | Tier III (51-70) | Water Exported (WE) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI)
Harris County Waterworks | GA1450011 | Harris | 42984 | 572.41 | 332.892 | 1.7306 | 908.7371 | 767.915 | Note 1 | 0.1058 | 11.3592 | 779.38 | 129.357 | 23.8845 | 105.4726 | 140.8221 | 510 | 9159 | 89.9232 | 4638380.66 | 6 | 1552.86 | 135.6516 | 140.82 | 143306.27 | 163784.27 | 324894.1 | VPC | 7.1445 | 31.5499 | 566.5999 | 33.5288 | 15.6465 | 17.8823 | 0.77753 | 64.1603 | Level III (51-75) | Water imported | Unbilled metered | Customer metering inaccuracies
Hart County Water and Sewer Authority | GA1470065 | Hart | 7353 | 0 | 335.428 | 21.774 | 314.2692 | 277.518 | 0 | 1.793 | 0.69379 | 280.0048 | 34.2644 | 2.5093 | 31.7551 | 36.7512 | 173.3 | 2828 | 95 | 2157475.94 | 5.48 | 2147.46 | 47.2188 | 36.7512 | 13727.08 | 68192.76 | 87260.13 | VPC | 2.431 | 30.7639 | 502.0208 | 28.9674 | 4.854 | 24.1134 | 0.67251 | 64 | Tier III (51-70) | Water Imported (WI) | Length of Mains (Lm) | Customer Metering Inaccuracies (CMI)
Hartwell | CS1470000 | Hart | 7116 | 592.466 | Note 1 | 138.1258 | 443.7486 | 394.8807 | Note 1 | 17.7013 | 1.0708 | 413.6528 | 30.0958 | 16.7046 | 13.3912 | 48.8679 | 85.115 | 2987 | 81.7177 | 2003041.17 | 5.25 | 338.18 | 27.0985 | 48.87 | 87699.34 | 4528.62 | 98576.29 | VPC | 15.3218 | 12.2826 | 431.0419 | 30.8765 | 29.3603 | 1.5161 | 0.49417 | 65.6576 | Level III (51-75) | Customer metering inaccuracies | Unbilled metered | Customer retail unit cost (applied to Apparent Losses)
Hawkinsville | GA2350001 | Pulaski | 6650 | 279.5334 | 0 | 0 | 276.7657 | 205.175 | 0 | 15.2498 | 0.51294 | 220.9377 | 55.828 | 1.0259 | 54.8021 | 71.5907 | 60 | 1847 | 55 | 948027.67 | 4.1 | 3391.46 | 12.0781 | 71.5907 | 4206.09 | 185859.23 | 243524.01 | VPC | 1.5217 | 81.2901 | 2502.3804 | 102.9049 | 2.2773 | 100.6276 | 4.5373 | 41 | Tier II (26-50) | Volume from Own Sources (VOS) | Length of Mains (Lm) | Number of Service Connections (Nc)
Hazlehurst | GA1610001 | Jeff Davis | 8058 | 305.859 | 0 | 0 | 321.2805 | 166.469 | 0 | 5.101 | 0.41617 | 171.9862 | 149.2943 | 9.8623 | 139.4319 | 154.8115 | 78 | 3099 | 51 | 1200000 | 2.68 | 169.34 | 16.5083 | 154.8115 | 25757.04 | 23611.41 | 50302.72 | VPC | 8.719 | 123.2673 | 4897.5042 | 15.9304 | 8.3114 | 7.619 | 8.4462 | 77 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Heard County Water Authority | GA1490000 | Heard | 8172 | 546.49 | 0.92993 | 61.5496 | 480.7206 | 221.909 | 0 | 6.4686 | 0.55477 | 228.9323 | 251.7883 | 13.1294 | 238.6589 | 258.8116 | 400 | 3890 | 80 | Note 5 | 9.99 | 874.66 | 80.227 | 258.8116 | 128059.55 | 208745.35 | 342947.94 | VPC | 9.247 | 168.0874 | 1634.6497 | 86.5822 | 32.9202 | 53.662 | 2.9748 | 67 | Tier III (51-70) | Customer Metering Inaccuracies (CMI) | Length of Mains (Lm) | Volume from Own Sources (VOS)
Henry County Water Authority | GA1510001 | Henry | 250000 | 6156.106 | 22.8676 | 535.7151 | 5627.8118 | 4973.7587 | 0 | 88.7648 | 20.9439 | 5083.4673 | 544.3445 | 92.8871 | 451.4574 | 654.0531 | 1364.552 | 71651 | 98.6 | 37382024 | 8.5376 | 336.38 | 652.4761 | 654.0531 | 781825.98 | 151861.24 | 970591.02 | VPC | 3.5517 | 17.2624 | 906.429 | 13.031 | 10.9116 | 2.1195 | 0.69191 | 89 | Tier IV (71-90) | Volume from Own Sources (VOS) | Water Exported (WE) | Unbilled Unmetered (UUAC)
Hephzibah Waterworks | GA2450002 | Richmond | 3830 | 193.965 | 0 | 0 | 204.1737 | 152.3856 | 0 | 0.342 | 0.38096 | 153.1086 | 51.0651 | 6.3013 | 44.7639 | 51.7881 | 50.4 | 1759 | 70 | 630377 | 2.94 | 578.62 | 13.7079 | 51.7881 | 18496.44 | 25901.26 | 44816.03 | VPC | 9.8145 | 69.7218 | 2433.3474 | 25.2403 | 10.5153 | 14.725 | 3.2655 | 64 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Hiawassee | GA2810000 | Towns | 5496 | 467.47 | 0 | 270.096 | 206.8382 | 126.338 | 0 | 2.536 | 0.31584 | 129.1898 | 77.6484 | 1.0065 | 76.6419 | 80.5002 | 75.4 | 2281 | 95 | 1217873 | 0.66 | 734.98 | 26.0085 | 80.5002 | 10656.21 | 56330.24 | 69082.5 | VPC | 1.2089 | 92.0551 | 2784.8506 | 29.3671 | 4.6717 | 24.6954 | 2.9468 | 67 | Tier III (51-70) | Water Exported (WE) | Volume from Own Sources (VOS) | Billed Metered (BMAC)
Hinesville | GA1790000 | Liberty | 24666 | 1270.948 | Note 1 | Note 1 | 1258.3644 | 1108.82 | 0.522 | 20.821 | 15.7296 | 1145.8926 | 112.4718 | 8.7491 | 103.7227 | 149.0224 | 208.5 | 14355 | 52 | 2114106 | 4.9 | 121.59 | 62.2778 | 149.02 | 42870.79 | 12611.64 | 59926.61 | VPC | 1.6698 | 19.796 | 1362.9337 | 3.865 | 2.9865 | 0.87855 | 1.6655 | 85.9495 | Level IV (75-90) | Volume from own sources | Unauthorized consumption | Systematic data handling errors
Hogansville | GA2850000 | Troup | 3866 | Note 1 | 128.266 | Note 1 | 127.6279 | 97.589 | Note 1 | Note 1 | 1.5953 | 99.1843 | 28.4435 | 5.1615 | 23.282 | 30.0389 | 31.3 | 1950 | 100 | 1065854 | 7.98 | 3345.52 | Note 3 | 30.04 | 41188.58 | 77890.52 | 124416.37 | VPC | 7.2518 | 32.711 | 2037.9041 | 61.0662 | 21.1223 | 39.9439 | Note 3 | 70.7003 | Level III (51-75) | Customer metering inaccuracies | Billed metered | Customer retail unit cost (applied to Apparent Losses)
Homerville | GA0650000 | Clinch | 3260 | 156.798 | Note 1 | Note 1 | 156.798 | 125.21 | Note 1 | 16.441 | 1.96 | 143.611 | 13.187 | 13.0225 | 0.16453 | 31.588 | 45 | 1375 | 45 | 306866 | 2.76 | 3.95 | Note 3 | 31.59 | 35942.1 | 0.65 | 36015.43 | VPC | 25.9477 | 0.32782 | 10.0168 | 26.1402 | 26.1397 | 0.00047273 | Note 3 | 60.1961 | Level III (51-75) | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Billed metered
Hoschton | GA1570002 | Jackson | 4459 | 33.807 | 74.192 | Note 1 | 109.1254 | 83.031 | Note 1 | 2.499 | 0.20758 | 85.7376 | 23.3879 | 0.67252 | 22.7154 | 26.0944 | 26.9 | 1661 | 38 | Note 5 | 13.17 | 1967.74 | 5.4742 | 26.0944 | 8772.81 | 44697.91 | 58796.56 | VPC | 1.1093 | 37.4677 | 2313.5257 | 32.1919 | 5.2816 | 26.9102 | 4.1495 | 65 | Tier III (51-70) | Length of Mains (Lm) | Customer Metering Inaccuracies (CMI) | Water Imported (WI)
Houston County - Feagin Mill System | GA1530021 | Houston | 163000 | 5042.363 | 0 | 1830.35 | 3074.0691 | 2389.832 | 30 | 0.6 | 22 | 2442.432 | 631.6371 | 36.2449 | 595.3921 | 654.2371 | 500 | 18542 | 65 | 7994186.67 | 1.66 | 305 | 130.1625 | 654.2371 | 60158.38 | 181594.6 | 248645.99 | VPC | 5.3555 | 87.9739 | 3262.4227 | 13.0381 | 3.2444 | 9.7937 | 4.5742 | 58 | Tier III (51-70) | Volume from Own Sources (VOS) | Water Exported (WE) | Billed Unmetered (BUAC)
Jackson County Water and Sewerage Utility | GA1570117 | Jackson | 24957 | Note 1 | 1440.474 | 465.527 | 974.201 | 645.359 | Note 1 | 242.579 | 12.1775 | 900.1155 | 74.0855 | 12.1129 | 61.9725 | 328.842 | 437.7 | 14994 | 102 | 10554.41 | 8.67 | 2488 | 171.893 | 328.84 | 105055.34 | 154187.66 | 893077.2 | VPC | 2.2133 | 11.3237 | 387.909 | 17.2898 | 7.0065 | 10.2833 | 0.36053 | 74.3814 | Level III (51-75) | Water imported | Billed metered | Customer metering inaccuracies
Jasper | GA2270000 | Pickens | 9600 | 584.68 | 137.7 | 26.5977 | 704.5954 | 369.29 | 0 | 0.9118 | 0.92323 | 371.125 | 333.4704 | 5.5859 | 327.8845 | 335.3054 | 196.5 | 5831 | 70 | 3567328 | 2.36 | 703.95 | 49.5086 | 335.3054 | 13167.38 | 230814.32 | 245273.47 | VPC | 2.6245 | 154.0583 | 4571.5715 | 41.8422 | 2.2582 | 39.584 | 6.6228 | 61 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Jefferson | GA1570003 | Jackson | 12000 | 519.185 | 23.447 | Note 1 | 550.616 | 433 | 0.03 | 20.233 | 6.268 | 459.531 | 91.085 | 9.0672 | 82.0178 | 117.586 | 129.37 | 5659 | 66 | Note 5 | 8.8 | 683.02 | 37.3092 | 117.586 | 77290.17 | 56019.82 | 151410.69 | VPC | 4.3897 | 39.7078 | 1736.928 | 23.5572 | 13.6579 | 9.8992 | 2.1983 | 74 | Tier IV (71-90) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Jesup Water System | GA3050000 | Wayne | 9952 | 456.277 | Note 1 | Note 1 | 455.775 | 395.44 | Note 1 | 28.497 | 0.9886 | 424.9256 | 30.8494 | 10.629 | 20.2204 | 60.335 | 136 | 4450 | 57.5 | 987100 | 3.04 | 221.98 | 29.4509 | 60.335 | 30673.21 | 4488.53 | 41706.95 | VPC | 6.5439 | 12.4491 | 407.3413 | 7.9015 | 6.8929 | 1.0087 | 0.68658 | 73 | Tier IV (71-90) | Customer Metering Inaccuracies (CMI) | Volume from Own Sources (VOS) | Billed Metered (BMAC)
Jones County Water System | GA1690002 | Jones | 13500 | 559.2927 | 0 | 107.285 | 465.9874 | 274.9141 | 0 | 0 | 0.68729 | 275.6013 | 190.386 | 1.3746 | 189.0114 | 191.0733 | 140.2235 | 4835 | 77 | Note 5 | 3.76 | 718.87 | 41.7039 | 191.0733 | 5168.38 | 135874.66 | 141537.11 | VPC | 0.77889 | 107.1023 | 3692.9587 | 29.1713 | 1.069 | 28.1023 | 4.5322 | 66 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Kingsland | GA0390000 | Camden | 19804 | 600.681 | Note 1 | Note 1 | 608.9629 | 587.856 | Note 1 | 0.552 | 7.612 | 596.02 | 12.9429 | 8.9356 | 4.0073 | 21.1069 | 181 | 8607 | 61.4 | 1311166.64 | 2.26 | 159.46 | 50.8788 | 21.11 | 20194.37 | 639 | 22135.21 | VPC | 2.8443 | 1.2756 | 60.6569 | 2.4205 | 2.3463 | 0.074242 | 0.078762 | 73.6594 | Level III (51-75) | Billed metered | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Lafayette | GA2950002 | Walker | 18177 | 749.96 | 407.569 | 0 | 1154.45 | 630.571 | 0 | 0.165 | 1.5764 | 632.3124 | 522.1376 | 8.4061 | 513.7315 | 523.879 | 638.8 | 8241 | 75 | Note 5 | 2.65 | 249.92 | 128.4451 | 523.879 | 22272.94 | 128391.77 | 151099.93 | VPC | 2.7946 | 170.7904 | 2203.3242 | 18.2823 | 2.7027 | 15.5796 | 3.9996 | 61 | Tier III (51-70) | Water Imported (WI) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI)
LaGrange | GA2850001 | Troup | 45230 | 2476.71 | Note 1 | 139.71 | 2337 | 1957.264 | Note 1 | Note 1 | 4.8932 | 1962.1572 | 374.8428 | 9.7863 | 365.0565 | 379.736 | 456.9 | 19701 | 89 | Note 5 | 3.3 | 416.96 | 176.2954 | 379.736 | 32294.86 | 152213.97 | 186549.07 | VPC | 1.3609 | 50.7667 | 2189.0016 | 9.3655 | 1.6392 | 7.7262 | 2.0707 | 68 | Tier III (51-70) | Volume from Own Sources (VOS) | Number of Service Connections (Nc) | Customer Retail Unit Charge (CRUC)
Lake Blackshear Area Water System | GA0810064 | Crisp | 4483 | 89.471 | 0 | 0 | 89.471 | 76.066 | 0 | 0.231 | 0.19017 | 76.4872 | 12.9838 | 0.38033 | 12.6035 | 13.405 | 112 | 1724 | 62 | 572174 | 3 | 233.3 | 19.5641 | 13.405 | 1140.99 | 2940.4 | 4179.65 | VPC | 0.60441 | 20.0291 | 308.3049 | 2.3674 | 0.66183 | 1.7056 | 0.64422 | 79 | Tier IV (71-90) | Customer Metering Inaccuracies (CMI) | Volume from Own Sources (VOS) | Billed Metered (BMAC)
Larchmont Utilities | GA0510034 | Chatham | 13780 | 420.461 | 0 | 0 | 420.461 | 370.369 | 0 | 2.664 | 0.92592 | 373.9589 | 46.5021 | 1.8518 | 44.6502 | 50.092 | 62 | 5300 | 48 | 2135969 | 6.25 | 209.04 | 19.805 | 50.092 | 11574.03 | 9333.68 | 21658.15 | VPC | 0.95727 | 23.081 | 1973.0549 | 3.9449 | 2.1838 | 1.7611 | 2.2545 | 73 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Lavonia | GA1190003 | Franklin | 8190 | 505.14 | 21.817 | 163.654 | 359.4986 | 236.157 | Note 1 | 9.982 | 4.4937 | 250.6327 | 108.8659 | 3.9754 | 104.8905 | 123.3416 | 127 | 8622 | 107 | 1508000 | 4.96 | 410.48 | 77.3434 | 123.34 | 19717.94 | 43055.45 | 68715.39 | VPC | 1.2632 | 33.33 | 2262.7656 | 7.2806 | 2.2869 | 4.9937 | 1.3562 | 58.6967 | Level III (51-75) | Volume from own sources | Water exported | Customer metering inaccuracies
Lee County Utilities Authority | GA1770068 | Lee | 17353 | 533.83 | 0 | 0 | 533.83 | 474.15 | 0 | 0.429 | 1.1854 | 475.7644 | 58.0656 | 27.3486 | 30.717 | 59.68 | 85 | 6674 | 68 | 2310000 | 2.61 | 277.85 | 36.2608 | 59.68 | 71327.17 | 8534.73 | 80310.45 | VPC | 11.2268 | 12.6096 | 990.0736 | 11.9661 | 10.6873 | 1.2788 | 0.84711 | 74 | Tier IV (71-90) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
Leesburg | GA1770000 | Lee | 3981 | 168.058 | 0 | 0 | 148.6042 | 118.407 | 0 | 26.3 | 0.29602 | 145.003 | 3.6012 | 0.35102 | 3.2502 | 30.1972 | 25.3 | 1531 | 62 | 249808 | 2.75 | 167.83 | 8.2944 | 30.1972 | 965.3 | 545.48 | 5974.39 | VPC | 0.62815 | 5.8162 | 351.9613 | 0.98679 | 0.6305 | 0.35629 | 0.39185 | 89 | Tier IV (71-90) | Volume from Own Sources (VOS) | Systematic Data Handling Errors (SDHE) | Unbilled Unmetered (UUAC)
Lincoln County BOC | GA1810038 | Lincoln | 3812 | 22.712 | 104.646 | Note 1 | 127.5504 | 61.819 | Note 1 | 0 | 0.15455 | 61.9735 | 65.5768 | 2.221 | 63.3558 | 65.7314 | 140.65 | 2208 | 75.5 | Note 5 | 14.38 | Note 2 | 30.096 | 65.7314 | 31938.31 | 0 | 31938.31 | VPC | 2.7559 | 78.613 | 1234.1103 | 14.4648 | 14.4648 | 0 | 2.1051 | 52 | Tier III (51-70) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Locust Grove | GA1510002 | Henry | 5648 | 181.314 | 113.489 | Note 1 | 296.8399 | 219.386 | Note 1 | 16.571 | 3.7105 | 239.6675 | 57.1724 | 3.0736 | 54.0988 | 77.4539 | 49.5 | 3787 | 60 | 1955822 | 8.89 | 1121.79 | 18.305 | 77.45 | 27324.44 | 60687.46 | 110763.48 | VPC | 2.2236 | 39.1381 | 2994.2589 | 23.2405 | 7.2153 | 16.0252 | 2.9554 | 62.7348 | Level III (51-75) | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Loganville | GA1350006 | Walton | 12319 | Note 1 | 463.904 | Note 1 | 459.3109 | 325.57 | Note 1 | 24.657 | 5.7414 | 355.9684 | 103.3425 | 9.1097 | 94.2328 | 133.7409 | 88.45 | 6048 | 80 | 3728466 | 29.86 | 3096 | 40.4629 | 133.74 | 272015.4 | 291744.79 | 657873.59 | VPC | 4.1267 | 42.6872 | 2918.8478 | 93.2143 | 44.9761 | 48.2382 | 2.3289 | 81.1947 | Level IV (75-90) | Water imported | Unauthorized consumption | Systematic data handling errors
Louisville | GA1630002 | Jefferson | 2605 | 379.098 | Note 1 | Note 1 | 380.9525 | 274.9596 | 0.092 | 13.962 | 1 | 290.0136 | 90.9389 | 1.3753 | 89.5637 | 105.9009 | 40.5 | 1554 | 42.6 | 658052 | 2.945 | 337.5696 | 7.0313 | 105.9009 | 4050.15 | 30233.97 | 39334.84 | VPC | 2.4246 | 157.9021 | 6058.7623 | 22.0619 | 2.6063 | 19.4556 | 12.7378 | 63 | Tier III (51-70) | Billed Unmetered (BUAC) | Customer Metering Inaccuracies (CMI) | Number of Service Connections (Nc)
Lowndes Co.-North Lowndes Co. WS | GA1850016 | Lowndes | 7194 | 462.757 | Note 1 | Note 1 | 461.757 | 442.109 | Note 1 | Note 1 | 1 | 443.109 | 18.648 | 3 | 15.648 | 19.648 | 112.4 | 5675 | 61 | 3501223 | 6.11 | 126.15 | 32.4921 | 19.65 | 18330 | 95609.28 | 114065.43 | CRUC | 1.4483 | 7.5544 | 381.4167 | 20.0774 | 3.23 | 16.8475 | 0.48159 | 68.8809 | Level III (51-75) | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | Volume from own sources
Lowndes Co.-South Lowndes Co. WS | GA1850019 | Lowndes | 7090 | 354.098 | Note 1 | Note 1 | 354.098 | 257.896 | Note 1 | Note 1 | 4.4262 | 262.3222 | 91.7758 | 1.53 | 90.2458 | 96.202 | 89.2 | 3301 | 61 | 2042381 | 6.11 | 588 | 21.769 | 96.2 | 9348.21 | 551401.78 | 563352.61 | CRUC | 1.2698 | 74.9012 | 2771.8469 | 169.8728 | 2.8319 | 167.0408 | 4.1456 | 71.1667 | Level III (51-75) | Billed metered | Variable production cost (applied to Real Losses) | Total annual cost of operating water system
Lyons | GA2790000 | Toombs | 4100 | 374.688 | Note 1 | Note 1 | 384.0984 | 236.161 | Note 1 | 31.581 | 4.8012 | 272.5432 | 111.5552 | 9.8313 | 101.7239 | 147.9374 | 42 | 8558 | 58 | 1722783 | 3 | 241.3 | 31.9862 | 147.94 | 29493.99 | 24545.97 | 62818.99 | VPC | 3.1474 | 32.5655 | 6635.6068 | 6.3146 | 3.4464 | 2.8682 | 3.1802 | 78.6056 | Level IV (75-90) | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Macon Water Authority | GA0210001 | Bibb | 135000 | 9351.63 | Note 1 | 271.76 | 8518.76 | 7330.6 | Note 1 | 247.11 | 38.04 | 7615.75 | 903.01 | 176.957 | 726.053 | 1188.16 | 1406.37 | 57960 | 121.9 | 18845191 | 4.49 | 670.39 | 725.3536 | 1188.16 | 1033922.35 | 486738.67 | 1711822.73 | VPC | 8.3646 | 34.32 | 1414.4118 | 26.2364 | 17.8385 | 8.3978 | 1.001 | 84 | Tier IV (71-90) | Billed Metered (BMAC) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI)
Madison | GA2110002 | Morgan | 5215 | 462.838 | Note 1 | 0.374 | 448.9776 | 329.901 | Note 1 | 16.04 | 5.6122 | 351.5532 | 97.4244 | 10.8175 | 86.6069 | 119.0766 | 75 | 3021 | 60 | 3613303 | 6.3 | 523.58 | 18.8099 | 119.08 | 68150.11 | 45345.63 | 124832.41 | VPC | 9.8103 | 78.5432 | 3163.7219 | 37.5689 | 22.5588 | 15.0101 | 4.6043 | 72.6457 | Level III (51-75) | Volume from own sources | Variable production cost (applied to Real Losses) | Customer retail unit cost (applied to Apparent Losses)
Madison County Water System | GA1950060 | Madison | 2964 | 133.3243 | 215.6408 | Note 1 | 361.6219 | 350.7043 | Note 1 | Note 1 | 0.87676 | 351.5811 | 10.0408 | 8.9108 | 1.1301 | 10.9176 | 103 | 1484 | 65 | Note 5 | 4.77 | 1896.94 | 18.5015 | 10.9176 | 42504.29 | 2143.67 | 46311.11 | VPC | 16.4508 | 2.0863 | 30.0589 | 30.0862 | 28.6417 | 1.4445 | 0.06108 | 56 | Tier III (51-70) | Water Imported (WI) | Length of Mains (Lm) | Customer Metering Inaccuracies (CMI)
Manchester Water Works | GA1990003 | Meriwether | 5343 | 489.65 | Note 1 | 30.3 | 459.35 | 378.589 | Note 1 | 2.5 | 5.7419 | 386.8309 | 72.5191 | 43.9681 | 28.551 | 80.761 | 113 | 2359 | 66 | 2290565 | 4.82 | 590.1 | 23.2512 | 80.76 | 211926.3 | 16847.95 | 233637.78 | VPC | 51.0643 | 33.1589 | 692.2297 | 96.9793 | 89.8373 | 7.142 | 1.2279 | 93.6275 | Level V (91-100) | Unauthorized consumption | Systematic data handling errors | Unbilled unmetered
Marietta Water/BLW | GA0670005 | Cobb | 60100 | Note 1 | 2703.138 | Note 1 | 2709.282 | 2458.016 | 0.0005913 | Note 1 | 33.866 | 2491.8826 | 217.3994 | 28.9999 | 188.3995 | 251.2654 | 307.871 | 19943 | 86 | 19802108 | 7.78 | 3558.93 | 146.1842 | 251.27 | 225619.06 | 670500.61 | 1016646.48 | VPC | 3.9839 | 25.8819 | 1676.5561 | 44.934 | 11.3132 | 33.6208 | 1.2888 | 79.5332 | Level IV (75-90) | Water imported | Billed metered | Unauthorized consumption
Marion County | GA1970003 | Marion | 5385 | 309.374 | Note 1 | Note 1 | 323.41 | 92.8822 | Note 1 | 0.0722 | 0.23221 | 93.1866 | 230.2234 | 2.3614 | 227.8619 | 230.5278 | 360 | 2674 | 62 | Note 5 | 2.35 | 505.63 | 53.1511 | 230.5278 | 5546.67 | 115213.83 | 120914.42 | VPC | 2.4195 | 233.4627 | 1734.1092 | 45.161 | 2.0743 | 43.0867 | 4.2871 | 55 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Length of Mains (Lm)
McCaysville | GA1110001 | Fannin | 7020 | 286.78 | Note 1 | Note 1 | 282.5419 | 127.618 | Note 1 | 1.288 | 3.5318 | 132.4378 | 150.1041 | 2.3275 | 147.7766 | 154.9239 | 151.5 | 3529 | 89 | 1496831 | 6.24 | 650.65 | 43.8211 | 154.92 | 14523.48 | 96150.86 | 113810.33 | VPC | 1.8069 | 114.7258 | 2672.3924 | 31.3614 | 4.1155 | 27.2459 | 3.3723 | 67.8884 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Billed metered
McDonough | GA1510003 | Henry | 8962 | 392.67 | 0.144 | Note 1 | 402.678 | 296.597 | Note 1 | Note 1 | 0.74149 | 297.3385 | 105.3395 | 6.3976 | 98.9418 | 106.081 | 90 | 6200 | 70.44 | 2934441 | 6.23 | 595.63 | 36.4293 | 106.081 | 39857.2 | 58932.73 | 99231.59 | VPC | 2.8271 | 43.7215 | 3011.9283 | 15.9339 | 6.4286 | 9.5053 | 2.716 | 77 | Tier IV (71-90) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
McRae Water System | GA2710003 | Telfair | 4907 | 244.603 | Note 1 | Note 1 | 244.603 | 227.553 | Note 1 | 2.02 | 0.56888 | 230.1419 | 14.4611 | 3.4567 | 11.0044 | 17.05 | 39.8 | 1964 | 56 | 400323.68 | 2.52 | 86.77 | 10.4227 | 17.05 | 8661.2 | 954.85 | 9840.69 | VPC | 4.822 | 15.3509 | 757.5159 | 4.8962 | 4.41 | 0.48618 | 1.0558 | 55 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Variable Production Cost (VPC)
Metter | GA0430000 | Candler | 4776 | 139.413 | Note 1 | Note 1 | 141.1634 | 115.928 | Note 1 | 1.62 | 1.7645 | 119.3125 | 21.8509 | 3.0417 | 18.8092 | 25.2354 | 63 | 2267 | 65 | 560205 | 4 | 288.06 | 16.1539 | 25.24 | 12166.67 | 5418.18 | 18559.8 | VPC | 3.6759 | 22.7314 | 817.9698 | 7.7569 | 5.3669 | 2.39 | 1.1644 | 79.2918 | Level IV (75-90) | Volume from own sources | Unauthorized consumption | Systematic data handling errors
Milledgeville | GA0090001 | Baldwin | 18738 | 1737.5 | Note 1 | 79.546 | 1657.954 | 763.979 | Note 1 | 3.461 | 1.9099 | 769.3499 | 888.6041 | 3.8199 | 884.7842 | 893.975 | 225 | 9187 | 70 | 5270147.75 | 4.7072 | 119.7622 | 66.3099 | 893.975 | 17980.87 | 105963.67 | 124587.78 | VPC | 1.1392 | 263.8583 | 10773.6275 | 13.4913 | 1.9572 | 11.5341 | 13.3432 | 42 | Tier II (26-50) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI)
Millen | GA1650000 | Jenkins | 5259 | 169.204 | Note 1 | Note 1 | 174.4371 | 125.532 | Note 1 | 3.889 | 2.1805 | 131.6015 | 42.8356 | 6.1425 | 36.6932 | 48.9051 | 50 | 2023 | 60 | 194309 | 2.25 | 381.82 | 12.5695 | 48.91 | 13820.55 | 14010.19 | 30148.18 | VPC | 8.3187 | 49.6932 | 2010.5855 | 13.7572 | 6.8317 | 6.9255 | 2.9192 | 49.0745 | Level II (26-50) | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Monroe | GA2970001 | Walton | 23376 | 962.12 | Note 1 | 113.09 | 825.61 | 690.26 | 9.62 | Note 1 | 10.3201 | 710.2001 | 115.4099 | 28.825 | 86.5849 | 125.73 | 228 | 10542 | 60 | 5790620.17 | 7.78 | 600.19 | 61.6437 | 125.73 | 224258.59 | 51967.37 | 282420 | VPC | 7.4912 | 22.5023 | 1040.4333 | 26.2024 | 21.2729 | 4.9296 | 1.4046 | 76.4501 | Level IV (75-90) | Variable production cost (applied to Real Losses) | Volume from own sources | Unauthorized consumption
Montezuma | GA1930003 | Macon | 3915 | 129.252 | Note 1 | Note 1 | 129.252 | 78.636 | Note 1 | Note 1 | 0.19659 | 78.8326 | 50.4194 | 0.39318 | 50.0262 | 50.616 | 38 | 1684 | 55 | Note 5 | 4 | 456.92 | 9.198 | 50.616 | 1572.72 | 22857.99 | 24520.53 | VPC | 0.63967 | 81.3885 | 3606.7938 | 14.5075 | 0.93392 | 13.5736 | 5.4388 | 71 | Tier IV (71-90) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
Monticello | GA1590000 | Jasper | 3505 | 172.56 | Note 1 | Note 1 | 176.0816 | 126.71 | Note 1 | 22.16 | 0.31677 | 149.1868 | 26.8949 | 0.63355 | 26.2613 | 49.3716 | 29.5 | 2085 | 75 | 860000 | 5.14 | 610.49 | 12.9304 | 49.3716 | 3256.45 | 16032.27 | 33010.56 | VPC | 0.8325 | 34.5078 | 2438.942 | 9.2512 | 1.5618 | 7.6893 | 2.031 | 34 | Tier II (26-50) | Volume from Own Sources (VOS) | Length of Mains (Lm) | Number of Service Connections (Nc)
Moultrie | GA0710004 / GA0710021 | Colquitt | 14638 | 1030.249 | Note 1 | Note 1 | 1051.2745 | 697.717 | Note 1 | Note 1 | 166.781 | 864.498 | 186.7765 | 25.0675 | 161.709 | 353.5575 | 220.9 | 8340 | 65 | Note 5 | 2.4 | 224.08 | 58.033 | 353.5575 | 60161.91 | 36235.76 | 133769.95 | VPC | 8.2348 | 53.1221 | 2005.6063 | 11.5585 | 7.2137 | 4.3448 | 2.7865 | 65 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Nashville | GA0190002 | Berrien | 4542 | 205.18 | Note 1 | Note 1 | 257.4404 | 168.871 | Note 1 | 1.296 | 3.218 | 173.385 | 84.0554 | 10.0219 | 74.0335 | 88.5694 | 85 | 2300 | 60 | 575000 | 3.69 | 2.32 | 17.6262 | 88.57 | 36980.95 | 171.76 | 37163.18 | VPC | 11.938 | 88.1876 | 2386.2517 | 16.1534 | 16.0787 | 0.074678 | 4.2002 | 57.7404 | Level III (51-75) | Volume from own sources | Master meter error adjustment | Total annual cost of operating water system
Newnan | GA077002 | Coweta | 50497 | 1727.48 | 43.955 | 407.679 | 1364.2045 | 1138.555 | Note 1 | 60.97 | 2.8464 | 1202.3714 | 161.8331 | 5.6928 | 156.1403 | 225.6495 | 263.6 | 20350 | 85 | 10597636 | 7.8 | 519.59 | 138.9478 | 225.6495 | 44403.65 | 81128.95 | 158690.95 | VPC | 0.76642 | 21.0212 | 1622.844 | 6.1687 | 2.182 | 3.9867 | 1.1237 | 77 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Newton County Water & Sewerage Authority | GA2170097 / GA2170004 | Newton | 190559 | Note 1 | 5080.149 | 3015.048 | 2065.101 | 1823.641 | Note 1 | 4.763 | 4.5591 | 1832.9631 | 232.1379 | 36.9619 | 195.176 | 241.46 | 647.49 | 27025 | 102 | 9071400 | 7.1 | 2240 | 281.3349 | 241.46 | 262077.13 | 437194.19 | 720152.82 | VPC | 3.7471 | 19.7864 | 825.8486 | 25.875 | 9.6976 | 16.1774 | 0.69375 | 57 | Tier III (51-70) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Water Exported (WE)
North Fulton County | GA1210005 | Fulton | 437032 | Note 1 | 9803.6 | 4.52 | 9792.22 | 8899.7 | Note 1 | 19.64 | 22.2493 | 8941.5893 | 850.6308 | 169.3078 | 681.323 | 892.52 | 1539 | 78855 | 98.1 | 28357481 | 4.1 | 590.57 | 721.6528 | 892.52 | 693197.34 | 402368.93 | 1120304.8 | VPC | 5.8824 | 23.6718 | 1212.8904 | 13.8934 | 8.7908 | 5.1026 | 0.94411 | 65 | Tier III (51-70) | Water Imported (WI) | Variable Production Cost (VPC) | Customer Metering Inaccuracies (CMI)
Notla Water Authority | GA2910003 | Union | 13465 | 329.476 | 0 | 0 | 329.476 | 235.235 | Note 1 | 1.362 | 20.741 | 257.338 | 72.138 | 1.5301 | 70.6079 | 94.241 | 546.54 | 6993 | 90 | 2441450.27 | 10.1 | 520.91 | 131.5883 | 94.24 | 15454.37 | 36780.34 | 63748.38 | VPC | 0.59948 | 27.6628 | 353.947 | 7.4696 | 2.21 | 5.2596 | 0.53658 | 79.1765 | Level IV (75-90) | Volume from own sources | Unauthorized consumption | Systematic data handling errors
Oconee County Water Resources Dept. | GA2190000 | Oconee | 21897 | 72.625 | 1047.483 | 79.816 | 1040.292 | 962.69 | 0 | 1.733 | 13.0037 | 977.4266 | 62.8653 | 5.0075 | 57.8579 | 77.602 | 351.7 | 11779 | 81.6 | 8811053 | 8.52 | 1454.91 | 109.2938 | 77.6 | 42663.52 | 84178.03 | 148282.56 | VPC | 1.1647 | 13.4574 | 450.7102 | 10.7684 | 3.622 | 7.1464 | 0.52938 | 54.8274 | Level III (51-75) | Water imported | Customer metering inaccuracies | Unbilled metered
Oglethorpe | GA1930003 | Macon | 6789 | 166.93 | Note 1 | Note 1 | 175.7158 | 142.17 | Note 1 | 0.662 | 0.35542 | 143.1874 | 32.5284 | 2.886 | 29.6424 | 33.5458 | 45.12 | 819 | 47.5 | 624555 | 2.66 | 387.91 | 6.362 | 33.5458 | 7653.74 | 11498.59 | 19546.99 | VPC | 9.6541 | 99.16 | 1799.913 | 23.385 | 9.3452 | 14.0398 | 4.6593 | 72 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Palmetto | GA1210008 | Fulton | 4718 | 88.6 | 61.239 | Note 1 | 148.9618 | 109.757 | Note 1 | 1.06 | 1.862 | 112.679 | 36.2828 | 3.4883 | 32.7945 | 39.2048 | 34.5 | 1651 | 55 | 753777.19 | 21.05 | 3459.63 | Note 3 | 39.2 | 73427.84 | 113456.81 | 196993.77 | VPC | 5.7885 | 54.4203 | 2604.2876 | 113.1948 | 44.4748 | 68.7201 | Note 3 | 58.6461 | Level III (51-75) | Volume from own sources | Water imported | Billed metered
Paulding County Water System | GA2230002 | Paulding | 165000 | 1201.475 | 3745.408 | 291.0299 | 4657.2968 | 3110.688 | Note 1 | Note 1 | 7.7767 | 3118.4647 | 1538.8321 | 111.7603 | 1427.0718 | 1546.6088 | 1005 | 55554 | 100 | Note 5 | 9.61 | 2921.16 | 502.6105 | 1546.6088 | 1074016.34 | 4168705.16 | 5265438.55 | VPC | 5.5116 | 70.3781 | 3890.3342 | 94.3716 | 19.3328 | 75.0388 | 2.8393 | 71 | Tier IV (71-90) | Customer Metering Inaccuracies (CMI) | Variable Production Cost (VPC) | Billed Metered (BMAC)
Pelham | GA2050003 | Mitchell | 6789 | 209.664 | Note 1 | Note 1 | 172.9188 | 115.875 | Note 1 | 0.771 | 0.28969 | 116.9357 | 55.9831 | 2.9599 | 53.0232 | 57.0438 | 47 | 1507 | 56 | 651531 | 2.65 | 501.86 | 9.8177 | 57.0438 | 7809.95 | 26610.21 | 34952.47 | VPC | 5.3811 | 96.3961 | 3090.8289 | 22.8402 | 5.1824 | 17.6577 | 5.4008 | 62 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Perry | GA1530006 | Houston | 19577 | 714.485 | Note 1 | Note 1 | 707.4067 | 567.8994 | Note 1 | Note 1 | 1.4197 | 569.3191 | 138.0875 | 8.5759 | 129.5116 | 139.5073 | 165.1 | 8473 | 61.86 | 2003633 | 3.775 | 209.358 | 48.8639 | 139.5073 | 32373.85 | 27114.3 | 59785.39 | VPC | 2.773 | 41.8773 | 2149.1607 | 7.0209 | 3.8208 | 3.2001 | 2.6505 | 73 | Tier IV (71-90) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC) | Volume from Own Sources (VOS)
Pickens County Water | GA2270002 | Pickens | 7153 | Note 1 | 304.671 | 77.065 | 231.796 | 190.51 | Note 1 | 0.178 | 0.47628 | 191.1643 | 40.6317 | 4.8441 | 35.7876 | 41.286 | 144.8 | 3685 | 110 | Note 5 | 5.12 | 290.44 | 53.6451 | 41.286 | 24784.46 | 10394.15 | 35368.64 | VPC | 3.6015 | 26.6074 | 677.1286 | 9.5464 | 6.7258 | 2.8207 | 0.66712 | 56 | Tier III (51-70) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Water Exported (WE)
Polk County Water Authority | GA2330001 | Polk | 23792 | 861.69 | 12.747 | 17.439 | 856.7481 | 554.07 | Note 1 | 11.116 | 10.7094 | 575.8954 | 280.8527 | 15.0615 | 265.7913 | 302.6781 | 500 | 10232 | 97 | 4166421 | 9.29 | 492.97 | 150.1101 | 302.68 | 139920.9 | 131027.11 | 281707.25 | VPC | 4.0329 | 71.1684 | 1456.3904 | 26.4805 | 13.6748 | 12.8056 | 1.7706 | 78.2264 | Level IV (75-90) | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Unauthorized consumption
Pooler | GA0510001 | Chatham | 26000 | 379.711 | 638.432 | 3.207 | 1020.5596 | 847.205 | Note 1 | 2.061 | 2.118 | 851.384 | 169.1756 | 4.236 | 164.9396 | 173.3546 | 116 | 11212 | 56 | 3550013 | 13.2 | 2086.99 | 47.2033 | 173.3546 | 55915.53 | 344227.2 | 408864.29 | VPC | 1.0351 | 40.3041 | 3895.5965 | 35.6888 | 4.9871 | 30.7017 | 3.4942 | 47 | Tier II (26-50) | Water Imported (WI) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI)
Port Wentworth | GA0510002 | Chatham | 5500 | 10.8961 | 345.6171 | Note 1 | 362.987 | 323.1584 | Note 1 | 11.1984 | 4.5373 | 338.8941 | 24.0929 | 1.7154 | 22.3775 | 39.8286 | 55 | 4512 | 62 | 2015196 | 2.29 | 2273.67 | 22.0495 | 39.83 | 3921.21 | 50879.14 | 90578.13 | VPC | 1.0416 | 13.5878 | 1114.6968 | 12.1455 | 0.86906 | 11.2764 | 1.0149 | 51.2035 | Level III (51-75) | Water imported | Customer metering inaccuracies | Total annual cost of operating water system
Quitman | GA0270002 | Brooks | 4870 | 620.136 | Note 1 | Note 1 | 613.996 | 178.348 | Note 1 | Note 1 | 7.675 | 186.023 | 427.9731 | 4.6968 | 423.2763 | 435.648 | 50 | 2741 | 62.3 | 1272270.39 | 3.18 | 52.29 | 15.5004 | 435.65 | 14935.89 | 22133.12 | 37470.33 | VPC | 4.6946 | 423.0795 | 23193.2203 | 13.5239 | 5.4491 | 8.0748 | 27.3075 | 70.1143 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Unauthorized consumption
Reynold Water System | GA1330046 | Greene | 10000 | 390.8 | Note 1 | Note 1 | 397.7608 | 332.5 | Note 1 | Note 1 | 0.83125 | 333.3313 | 64.4296 | 5.0211 | 59.4085 | 65.2608 | 221.4 | 4126 | 77 | Note 5 | 12.65 | 1513.84 | 51.0576 | 65.2608 | 63516.74 | 89934.93 | 154710.05 | VPC | 3.3341 | 39.4481 | 735.1534 | 37.1914 | 15.3943 | 21.7971 | 1.1636 | 41 | Tier II (26-50) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Variable Production Cost (VPC)
Richmond Hill | GA0290000 | Bryan | 12594 | 751.178 | Note 1 | Note 1 | 751.1592 | 585.59 | Note 1 | 1.42 | 9.3895 | 596.3995 | 154.7597 | 9.2713 | 145.4885 | 165.5692 | 98.34 | 7151 | 52 | 100356 | 3.4 | 133.63 | 30.4566 | 165.57 | 31522.31 | 19441.62 | 52408.4 | VPC | 3.5521 | 55.7403 | 4053.2696 | 7.1268 | 4.4081 | 2.7187 | 4.7769 | 69.5485 | Level III (51-75) | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Rincon | GA1030001 | Effingham | 9880 | 342.208 | Note 1 | Note 1 | 342.208 | 289.124 | Note 1 | 8.653 | 4.2776 | 302.0546 | 40.1534 | 4.5862 | 35.5672 | 53.084 | 1381.5 | 4722 | 65 | 113500 | 4.5 | 394.54 | 194.1231 | 53.08 | 20637.8 | 14032.69 | 39772.13 | VPC | 2.6609 | 20.6363 | 70.5352 | 7.3423 | 4.3706 | 2.9718 | 0.18322 | 66.2353 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Ringgold | GA0470002 | Catoosa | 3681 | 145.9 | 29 | Note 1 | 176.9656 | 144.021 | Note 1 | 7.596 | 0.36005 | 151.9771 | 24.9885 | 0.87187 | 24.1166 | 32.9446 | 28 | 1377 | 99.8 | 529292 | 4.8 | 359.81 | 13.042 | 32.9446 | 4151.23 | 8677.41 | 15691.31 | VPC | 1.7347 | 47.9833 | 2359.7503 | 9.3164 | 3.0147 | 6.3017 | 1.8492 | 76 | Tier IV (71-90) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Rockdale County Water Resources | GA2470000 | Rockdale | 87000 | 4059.84 | Note 1 | Note 1 | 4185.4021 | 2897.67 | Note 1 | 33.694 | 7.2442 | 2938.6082 | 1246.7939 | 44.0981 | 1202.6958 | 1287.7321 | 670 | 29446 | 100 | 15792609 | 6.826 | 231.97 | 293.5184 | 1287.7321 | 298769.31 | 278989.34 | 587255.08 | VPC | 4.103 | 111.9017 | 4917.9955 | 19.621 | 10.1463 | 9.4746 | 4.0975 | 72 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Rockmart | GA2330002 | Polk | 4199 | 515.32 | Note 1 | Note 1 | 515.5262 | 376.678 | Note 1 | 5.789 | 0.9417 | 383.4087 | 132.1175 | 10.0875 | 122.03 | 138.8482 | 67.5 | 3312 | 60 | 1884470.49 | 5.79 | 298 | 18.8773 | 138.8482 | 57724.55 | 36364.95 | 96095.24 | VPC | 8.3445 | 100.9447 | 4953.0201 | 28.4087 | 17.4289 | 10.9798 | 6.4644 | 64 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Rome | GA1150002 | Floyd | 45586 | 2335 | Note 1 | 142 | 2193 | 1743 | 2.4 | 116 | 50.1 | 1911.5 | 281.5 | 113.3575 | 168.1425 | 447.6 | 298 | 18985 | 85 | 5892709 | 3.73 | 550 | 138.3693 | 447.6 | 422788.05 | 92478.38 | 606621.43 | VPC | 16.3586 | 24.2647 | 1545.8536 | 27.1407 | 22.2696 | 4.8711 | 1.2152 | 76.7204 | Level IV (75-90) | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered
Roswell | GA1210009 | Fulton | 18453 | 631.79 | 2.33 | Note 1 | 634.2582 | 487.559 | Note 1 | 7.296 | 1.321 | 496.176 | 138.0822 | 7.0568 | 131.0254 | 146.6992 | 89 | 5804 | 88.8 | 4887662 | 9 | 391.48 | 43.8239 | 146.6992 | 62924.9 | 51293.83 | 117592.12 | VPC | 3.3311 | 61.8494 | 4033.4131 | 19.6793 | 10.8416 | 8.8377 | 2.9898 | 85 | Tier IV (71-90) | Volume from Own Sources (VOS) | Customer Retail Unit Charge (CRUC) | Unauthorized Consumption (UC)
Sandersville | GA3030005 | Washington | 6045 | 684.4405 | Note 1 | 95.8484 | 582.9426 | 299.841 | Note 1 | 13.1101 | 0.7496 | 313.7007 | 269.2419 | 1.4992 | 267.7427 | 283.1016 | 70.3 | 2839 | 54.3684 | 978866.4 | 5.9168 | 86.2782 | 15.9981 | 283.1016 | 8870.5 | 23100.36 | 33166.65 | VPC | 1.4468 | 258.3803 | 10434.4479 | 11.2613 | 3.1245 | 8.1368 | 16.7359 | 61 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Number of Service Connections (Nc)
Satilla Regional Water & Sewer Authority / Satilla Regional Water & Sewer Authority-East | GA2990001 / GA2990051 | Ware | 14311 | 381.652 | Note 1 | Note 1 | 385.5071 | 354.907 | Note 1 | Note 1 | 4.8188 | 359.7258 | 25.7812 | 3.6345 | 22.1467 | 30.6001 | 236 | 6860 | 52 | 1850177 | 2.8 | 252.52 | 43.7633 | 30.6 | 10176.56 | 5592.5 | 16985.91 | VPC | 1.4515 | 8.8449 | 257.1018 | 2.2987 | 1.4835 | 0.81523 | 0.50606 | 80.9 | Level IV (75-90) | Customer retail unit cost (applied to Apparent Losses) | Volume from own sources | Unauthorized consumption
Savanna-Georgetown Gateway | GA0510081 | Chatham | 16291 | 622.9399 | Note 1 | Note 1 | 622.9399 | 574.296 | Note 1 | 1.2036 | 1.4357 | 576.9353 | 46.0046 | 13.958 | 32.0466 | 48.6439 | 102 | 6345 | 52.068 | 1739723.75 | 2.67 | 222.48 | 28.5751 | 48.6439 | 49742.13 | 7129.74 | 57459.07 | VPC | 6.0269 | 13.8375 | 860.7745 | 8.9633 | 7.8396 | 1.1237 | 1.1215 | 59 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Retail Unit Charge (CRUC) | Billed Metered (BMAC)
Savannah-Main | GA0510003 | Chatham | 153355 | 5137.4847 | 964.796 | 19.961 | 6066.9534 | 5014.1918 | Note 1 | 185.438 | 12.5355 | 5212.1653 | 854.7881 | 125.3992 | 729.3889 | 1052.7615 | 690 | 60555 | 55.5 | 13393417.87 | 1.81 | 169.25 | 259.6232 | 1052.7615 | 295366.1 | 123449.08 | 452322.18 | VPC | 5.6735 | 33.0002 | 2896.1244 | 6.9163 | 4.8777 | 2.0386 | 2.8094 | 58 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Unauthorized Consumption (UC)
Savannah-Quarters | GA0510259 | Chatham | 2818 | 116.6083 | Note 1 | 9.2624 | 105.8494 | 83.8005 | Note 1 | 2.8628 | 0.2095 | 86.8728 | 18.9766 | 2.0885 | 16.8881 | 22.0489 | 18.26 | 1088 | 56.87 | 319105 | 2.77 | 297 | 5.4382 | 22.0489 | 5648.74 | 5015.77 | 11576.98 | VPC | 5.2591 | 42.5265 | 2533.8873 | 9.8019 | 5.1919 | 4.6101 | 3.1055 | 62 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Savannah-Whitemarsh | GA0510250 | Chatham | 4479 | 237.3185 | Note 1 | Note 1 | 237.3185 | 196.4811 | Note 1 | 0.27454 | 0.4912 | 197.2468 | 40.0717 | 4.7727 | 35.299 | 40.8374 | 25.33 | 1712 | 59.94 | 579702.07 | 2.61 | 176.75 | 8.6164 | 40.8374 | 16634.81 | 6239.09 | 23009.25 | VPC | 7.6378 | 56.4892 | 3817.9835 | 13.3609 | 9.7166 | 3.6443 | 4.0967 | 61 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Customer Retail Unit Charge (CRUC)
Savannah-Wilmington | GA0510229 | Chatham | 13980 | 484.8564 | Note 1 | Note 1 | 484.8564 | 376.538 | Note 1 | 3.2802 | 0.94134 | 380.7595 | 104.0969 | 9.1995 | 94.8974 | 108.3184 | 58 | 5389 | 53.55 | 1219874.35 | 2.84 | 128.71 | 21.9329 | 108.3184 | 34694.55 | 12214.24 | 47452.14 | VPC | 4.677 | 48.2451 | 4482.6336 | 8.7045 | 6.438 | 2.2665 | 4.3267 | 58 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Retail Unit Charge (CRUC) | Billed Metered (BMAC)
Senoia | GA0770003 | Coweta | 5016 | 100.514 | 70.186 | Note 1 | 170.7 | 159.672 | Note 1 | 4.162 | 0.646 | 164.48 | 6.22 | 5.8654 | 0.35461 | 11.028 | 65 | 2900 | 64.6 | Note 5 | 8.08 | 1688.37 | 18.5484 | 11.028 | 46569.62 | 598.71 | 55286.01 | VPC | 5.5412 | 0.33501 | 14.9466 | 16.2649 | 16.0585 | 0.20645 | 0.019118 | 44 | Tier II (26-50) | Volume from Own Sources (VOS) | Water Imported (WI) | Billed Metered (BMAC)
Smyrna | GA0670007 | Cobb | 35000 | Note 1 | 1440.301 | Note 1 | 1449.4324 | 1222.629 | 8.92 | 14.154 | 18.1179 | 1263.8209 | 185.6115 | 28.8375 | 156.774 | 217.8834 | 185.5 | 15737 | 113.5 | 12243373 | 5.53 | 3194.1 | 139.3665 | 217.88 | 159471.4 | 500751.88 | 763302.97 | VPC | 5.0205 | 27.2935 | 2315.4601 | 41.9536 | 10.1335 | 31.82 | 1.1249 | 75.9343 | Level III (51-75) | Customer metering inaccuracies | Billed metered | Water imported
Social Circle | GA2970002 | Walton | 4200 | 175.06 | 94.693 | Note 1 | 273.4538 | 142.652 | Note 1 | 5.451 | 0.35663 | 148.4596 | 124.9941 | 2.9686 | 122.0255 | 130.8018 | 24.5 | 2502 | 60 | Note 5 | 19.15 | 1248.04 | 11.1218 | 130.8018 | 55363.33 | 152292.72 | 214904.21 | VPC | 3.2507 | 133.6197 | 13645.5703 | 82.996 | 22.1276 | 60.8684 | 10.9717 | 62 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Water Imported (WI)
South Atlantic Utilities-Bryan County | GA0290080 | Bryan | 3424 | 103.763 | Note 1 | Note 1 | 103.763 | 100.095 | Note 1 | Note 1 | 0.25024 | 100.3452 | 3.4178 | 0.50048 | 2.9173 | 3.668 | 12 | 1317 | 45 | Note 5 | 3.5 | 293.812 | 4.3111 | 3.668 | 1751.66 | 857.13 | 2682.32 | VPC | 1.0411 | 6.0688 | 666.0474 | 1.9809 | 1.33 | 0.65082 | 0.6767 | 51 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
South Monroe County Water System | GA2070074 | Monroe | 8580 | Note 1 | 292.922 | 7.158 | 285.764 | 191.413 | Note 1 | 3.6 | 5.533 | 200.546 | 85.218 | 0.95707 | 84.2609 | 94.351 | 101 | 4533 | 64 | Note 5 | 7.59 | 2827 | 28.6478 | 94.351 | 7264.12 | 238205.66 | 271288.78 | VPC | 0.57845 | 50.927 | 2285.6621 | 54.1517 | 1.6025 | 52.5492 | 2.9413 | 52 | Tier III (51-70) | Water Imported (WI) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI)
Spalding County Water System | GA2550036 | Spalding | 40430 | Note 1 | 1015.348 | Note 1 | 1015.348 | 799.659 | Note 1 | 33.411 | 14.086 | 847.156 | 168.192 | 12.8674 | 155.3246 | 215.689 | 523 | 14430 | 99 | 8778383.91 | 10.85 | Note 2 / B | 180.4557 | 215.69 | 139611.03 | Note 4 | 139611.03 | CRUC | 2.443 | 29.4904 | 813.6652 | 9.6751 | 9.6751 | 0 | 0.86074 | 53.9706 | Level III (51-75) | Water imported | Billed metered | Unauthorized consumption
Sparta | GA1410001 | Hancock | 3710 | 350.28 | Note 1 | 34.589 | 318.2384 | 222.7813 | Note 1 | 5.2063 | 0.55695 | 228.5445 | 89.6939 | 4.5858 | 85.1081 | 95.4572 | 53 | 1714 | 59 | Note 5 | 8.74 | 739.26 | 11.7114 | 95.4572 | 39445.55 | 62917.02 | 106623.11 | VPC | 7.3301 | 136.0402 | 4399.4883 | 59.7215 | 23.0137 | 36.7077 | 7.2671 | 62 | Tier III (51-70) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI) | Volume from Own Sources (VOS)
St. Marys | GA0390001 | Camden | 19800 | 522.312 | Note 1 | Note 1 | 522.312 | 470.2139 | Note 1 | Note 1 | 1.1755 | 471.3894 | 50.9226 | 2.3511 | 48.5715 | 52.0981 | 131 | 8220 | 55.5 | Note 5 | 3.07 | 328.31 | 39.3342 | 52.0981 | 7217.78 | 15946.51 | 23550.23 | VPC | 0.78361 | 16.1889 | 1015.8213 | 2.818 | 0.87808 | 1.94 | 1.2348 | 51 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Statesboro | GA0310004 | Bulloch | 36846 | 1306.759 | Note 1 | Note 1 | 1296.362 | 1171.391 | Note 1 | Note 1 | 16.2045 | 1187.5955 | 108.7665 | 18.0016 | 90.7649 | 124.971 | 250.1 | 14636 | 62.3 | 1982742.59 | 4.04 | 240.62 | 80.6898 | 124.97 | 72726.52 | 21839.84 | 98465.49 | VPC | 3.3697 | 16.9904 | 994.2857 | 6.4612 | 4.969 | 1.4922 | 1.1249 | 65.5619 | Level III (51-75) | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Statham | GA0130001 | Barrow | 2813 | 41.009 | 74.127 | Note 1 | 117.8428 | 91.528 | Note 1 | 0.84931 | 0.22882 | 92.6061 | 25.2367 | 3.3147 | 21.9221 | 26.3149 | 49.82 | 1871 | 83 | Note 5 | 14.32 | 2819.69 | 16.6676 | 26.3149 | 47163.98 | 61813.4 | 112017.37 | VPC | 4.8537 | 32.1007 | 1205.5485 | 58.2455 | 25.2079 | 33.0376 | 1.3153 | 59 | Tier III (51-70) | Water Imported (WI) | Volume from Own Sources (VOS) | Customer Retail Unit Charge (CRUC)
Stockbridge | GA1510004 | Henry | 7195 | 95.001 | 180.5459 | Note 1 | 283.5115 | 216.888 | Note 1 | 10.609 | 6.28 | 233.777 | 49.7345 | 5.7272 | 44.0072 | 66.6235 | 49 | 2754 | 92.2 | Note 5 | 8.1255 | 2698.17 | 22.8231 | 66.6235 | 45361.76 | 118738.96 | 209670.11 | VPC | 5.6976 | 43.7791 | 2460.5657 | 59.5863 | 16.4712 | 43.1151 | 1.9282 | 63 | Tier III (51-70) | Water Imported (WI) | Volume from Own Sources (VOS) | Number of Service Connections (Nc)
Summerville | GA0550003 | Chattooga | 11651 | 749.462 | Note 1 | Note 1 | 724.1179 | 526.845 | Note 1 | Note 1 | 9.0515 | 535.8965 | 188.2214 | 22.2358 | 165.9856 | 197.2729 | 225 | 5198 | 80 | 2115000 | 6.05 | 397.63 | 58.3109 | 197.27 | 134526.44 | 66000.86 | 204126.44 | VPC | 11.7199 | 87.4866 | 2021.134 | 38.5778 | 25.8804 | 12.6974 | 2.8466 | 62.7444 | Level III (51-75) | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses)
Swainsboro | GA1070031 | Emanuel | 8500 | 408.4888 | Note 1 | Note 1 | 408.4888 | 233.9338 | Note 1 | 2.333 | 0.58483 | 236.8516 | 171.6372 | 3.5562 | 168.081 | 174.5551 | 97.15 | 3601 | 52 | Note 5 | 7.22 | 55.14 | 20.2276 | 174.5551 | 25506.93 | 9267.99 | 34935.81 | VPC | 2.7056 | 127.88 | 4740.0509 | 9.657 | 7.0833 | 2.5737 | 8.3095 | 64 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Sylvania | GA2510003 | Screven | 4910 | 249.07 | Note 1 | Note 1 | 252.0951 | 151.418 | Note 1 | Note 1 | 3.1512 | 154.5692 | 97.526 | 8.9782 | 88.5478 | 100.6771 | 127 | 1655 | 60 | 1158349.5 | 4.44 | 371.57 | 20.4835 | 100.68 | 39862.99 | 32901.71 | 73935.59 | VPC | 14.8626 | 146.5841 | 1910.2104 | 43.9666 | 24.0864 | 19.8802 | 4.3229 | 38.2866 | Level II (26-50) | Volume from own sources | Customer metering inaccuracies | Total annual cost of operating water system
Sylvester | GA3210003 | Worth | 6923 | 312.134 | Note 1 | Note 1 | 321.7876 | 207.274 | Note 1 | Note 1 | 4.0223 | 211.2963 | 110.4913 | 4.4791 | 106.0122 | 114.5136 | 82 | 3080 | 80 | 1290860.64 | 5.21 | 367.25 | 26.4441 | 114.51 | 23336.17 | 38932.97 | 63746.35 | VPC | 3.9843 | 94.3001 | 3542.0038 | 20.2173 | 7.5767 | 12.6406 | 4.0089 | 73.185 | Level III (51-75) | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | Billed metered
Talbot County Water Works | GA2630005 | Talbot | 3875 | Note 1 | 171.474 | 50.1169 | 123.3066 | 68.4513 | Note 1 | 1.167 | 0.17113 | 69.7894 | 53.5172 | 4.0064 | 49.5108 | 54.8553 | 150 | 1579 | 70 | 1013731.93 | 15.02 | 3050.21 | 26.7853 | 54.8553 | 59440.58 | 151018.34 | 214540.37 | VPC | 6.9515 | 85.9063 | 904.3068 | 133.2862 | 37.6444 | 95.6418 | 1.8484 | 51 | Tier III (51-70) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Length of Mains (Lm)
Tallapoosa | GA1430002 | Haralson | 4680 | Note 1 | 182.715 | Note 1 | 186.4439 | 132.87 | Note 1 | Note 1 | 0.33217 | 133.2022 | 53.2417 | 0.69093 | 52.5508 | 53.5739 | 31 | 1743 | 80 | Note 5 | 7.55 | 2920 | 12.5315 | 53.5739 | 5216.52 | 153448.26 | 159634.73 | VPC | 1.086 | 82.6017 | 4644.3458 | 91.0297 | 2.9928 | 88.0369 | 4.1935 | 67 | Tier III (51-70) | Water Imported (WI) | Length of Mains (Lm) | Unauthorized Consumption (UC)
Temple | GA0450005 | Carroll | 4500 | Note 1 | 162.69 | Note 1 | 162.69 | 127.92 | Note 1 | 0.49 | 2.0336 | 130.4436 | 32.2464 | 5.3839 | 26.8625 | 34.77 | 44 | 2547 | 50 | 1763265 | 6.08 | 3114.17 | 11.3166 | 34.77 | 32734.01 | 83654.37 | 124247.38 | VPC | 5.7913 | 28.8951 | 1672.6334 | 45.6963 | 12.852 | 32.8443 | 2.3737 | 49.8725 | Level II (26-50) | Water imported | Billed metered | Customer metering inaccuracies
The Landings Subdivision | GA0510033 | Chatham | 12100 | 500.995 | Note 1 | Note 1 | 499.156 | 449.654 | Note 1 | 0.178 | 1.19 | 451.022 | 48.134 | 5.8679 | 42.2661 | 49.502 | 95.4 | 4713 | 56.6 | 779645 | 4.9 | 498.5 | 25.2673 | 49.502 | 28744.76 | 207103.93 | 242551.89 | CRUC | 3.4111 | 24.5698 | 1213.8108 | 50.0422 | 6.099 | 43.9431 | 1.6728 | 84 | Tier IV (71-90) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Systematic Data Handling Errors (SDHE)
Thomaston | GA2930000 | Upson | 12482 | 559.78 | Note 1 | 33.98 | 525.8 | 381.373 | Note 1 | 39.089 | 0.95343 | 421.4154 | 104.3846 | 6.154 | 98.2306 | 144.427 | 114 | 4928 | 83 | 2552713.29 | 7.43 | 1423.02 | 46.3798 | 144.427 | 43352.11 | 139784.12 | 240117.41 | VPC | 3.4213 | 54.6114 | 2360.7453 | 37.1624 | 8.7971 | 28.3653 | 2.118 | 67 | Tier III (51-70) | Customer Metering Inaccuracies (CMI) | Volume from Own Sources (VOS) | Billed Metered (BMAC)
Thomasville | GA2750005 | Thomas | 24206 | 1974.861 | Note 1 | Note 1 | 1940.8953 | 1372.859 | Note 1 | 3.2 | 24.2612 | 1400.3202 | 540.5751 | 43.5679 | 497.0072 | 568.0363 | 271.04 | 14110 | 66.4 | 4630015 | 6.43 | 4.08 | 86.8334 | 568.04 | 280141.92 | 2027.79 | 282281.75 | VPC | 8.4595 | 96.5034 | 5023.8472 | 19.9979 | 19.8541 | 0.14371 | 5.7237 | 75.7941 | Level III (51-75) | Volume from own sources | Billed metered | Unauthorized consumption
Thomson-McDuffie Co. W&S Comm | GA1890001 | McDuffie | 17717 | 640.19 | Note 1 | Note 1 | 640.19 | 496.721 | Note 1 | Note 1 | 28.5 | 525.221 | 114.969 | 12.6208 | 102.3482 | 143.469 | 280 | 7455 | 62 | 3766869 | 8.6935 | 655.62 | 59.5859 | 143.469 | 109718.24 | 67101.55 | 195504.95 | VPC | 4.6382 | 37.6132 | 1001.4504 | 23.7183 | 14.7174 | 9.0009 | 1.7177 | 67 | Tier III (51-70) | Volume from Own Sources (VOS) | Variable Production Cost (VPC) | Billed Metered (BMAC)
Tifton-Tift County Water System | GA2770001 | Tift | 30940 | 1644.976 | Note 1 | Note 1 | 1644.976 | 1278.661 | Note 1 | Note 1 | 3.1967 | 1281.8577 | 363.1183 | 36.4948 | 326.6235 | 366.315 | 286.5 | 12142 | 58.7 | 3582800 | 1.43 | 250.08 | 72.231 | 366.315 | 52187.63 | 81682.01 | 134669.05 | VPC | 8.2347 | 73.6995 | 3123.4168 | 11.0253 | 4.2981 | 6.7272 | 4.5219 | 64 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Variable Production Cost (VPC)
Toccoa | GA2570001 | Stephens | 24960 | 1380.84 | Note 1 | 405.831 | 975.009 | 671.593 | Note 1 | 113.1 | 0.117 | 784.81 | 190.199 | 25.9623 | 164.2367 | 303.416 | 613.7 | 11298 | 125 | 1456655.8 | 7.21 | 362.13 | 228.801 | 303.416 | 164877.58 | 59475.04 | 265351.89 | VPC | 6.2958 | 39.8268 | 733.198 | 19.8577 | 14.5935 | 5.2642 | 0.71781 | 63 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Water Exported (WE)
Towns County Water & Sewerage Authority | GA2810007 | Towns | 11000 | Note 1 | 270.096 | Note 1 | 270.3393 | 152.412 | Note 1 | 0.03268 | 3.4819 | 155.9266 | 114.4127 | 1.2901 | 113.1227 | 117.9273 | 204 | 4550 | 100 | 2087183 | 6.39 | 2437.16 | 65.1941 | 117.9273 | 8243.04 | 275698.04 | 292506.66 | VPC | 0.77679 | 68.1154 | 1519.2407 | 62.4046 | 1.8117 | 60.593 | 1.7352 | 63 | Tier III (51-70) | Water Imported (WI) | Length of Mains (Lm) | Customer Metering Inaccuracies (CMI)
Tybee Island | GA0510005 | Chatham | 8047 | 290.236 | Note 1 | Note 1 | 289.5122 | 272.426 | Note 1 | 0.537 | 3.6189 | 276.5819 | 12.9303 | 2.089 | 10.8414 | 17.0862 | 33.9 | 3350 | 60 | 1724699 | 4.34 | 112.16 | 15.0212 | 17.09 | 9066.1 | 1215.97 | 10748.2 | VPC | 1.7084 | 8.8664 | 876.1752 | 3.0693 | 2.7063 | 0.36298 | 0.72174 | 69.659 | Level III (51-75) | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses)
Unadilla | GA0930003 | Dooly | 3806 | 207.93 | Note 1 | Note 1 | 207.93 | 133.35 | Note 1 | 15.25 | 0.33337 | 148.9334 | 58.9966 | 0.66675 | 58.3299 | 74.58 | 35.1 | 1464 | 65 | 388424.5 | 4 | 376.82 | 9.7152 | 74.58 | 2667 | 21979.86 | 30518.99 | VPC | 1.2478 | 109.1584 | 4552.931 | 16.8353 | 1.8217 | 15.0136 | 6.004 | 65 | Tier III (51-70) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
Union City | GA1210010 | Fulton | 18636 | Note 1 | 547.297 | Note 1 | 563.2366 | 235.576 | Note 1 | 179.41 | 0.6819 | 415.6679 | 147.5687 | 9.647 | 137.9217 | 327.6606 | 72.22 | 7126 | 128 | 5519194.77 | 11.22 | 4823.38 | 68.193 | 327.6606 | 84818.37 | 665248.84 | 1618718.87 | VPC | 3.709 | 53.0266 | 5232.1754 | 105.2578 | 11.9027 | 93.3552 | 2.0225 | 69 | Tier III (51-70) | Water Imported (WI) | Unbilled Metered (UMAC) | Unauthorized Consumption (UC)
Upson County Water Department | GA2930010 | Upson | 5049 | 147.335 | 9.29 | Note 1 | 158.9013 | 136.242 | Note 1 | 0.835 | 0.3406 | 137.4176 | 21.4837 | 4.9207 | 16.563 | 22.6593 | 71.6 | 2406 | 82.3 | 1060450 | 9.55 | 2418.19 | 22.4772 | 22.6593 | 46808.55 | 40052.48 | 89703.87 | VPC | 5.6032 | 18.8604 | 633.7721 | 36.1018 | 19.4549 | 16.6469 | 0.73688 | 68 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Metered (BMAC) | Customer Retail Unit Charge (CRUC)
USAF-Moody Air Force Base Main | GA1850125 | Lowndes | 6109 | 106.362 | Note 1 | Note 1 | 106.362 | 7.745 Note A | Note 1 | 11.12 | 1.3295 | 20.1945 | 86.1675 | 0.47582 | 85.6917 | 98.617 | 50.8 | 490 | 65 | 159700 | 2.97 | 331.26 | Note 3 | 98.62 | 1413.19 | 28386.22 | 33923.44 | VPC | 2.6605 | 479.1258 | 4621.4892 | 60.8151 | 2.8841 | 57.9311 | Note 3 | 58.2745 | Level III (51-75) | Volume from own sources | Billed metered | Customer metering inaccuracies
USA-Fort Stewart Main | GA1790024 | Liberty | 27573 | 659.9 | Note 1 | Note 1 | 659.9 | 29 | 310.3 | Note 1 | 315 | 654.3 | 5.6 | 1.7692 | 3.8308 | 320.6 | 161.7 | 2677 | 57 | 972027 | 14.43 | 1443 | 28.9278 | 320.6 | 25529.29 | 5527.87 | 485602.16 | VPC | 1.8106 | 3.9206 | 64.9066 | 11.6015 | 9.5365 | 2.0649 | 0.13243 | 60 | Tier III (51-70) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI) | Billed Unmetered (BUAC)
USAF-Robins Air Force Base Main | GA1530042 | Houston | 23967 | 536.6 | Note 1 | Note 1 | 536.6 | 88.98 | 364.33 | 7.195 | 6.7075 | 467.2125 | 69.3875 | 4.03 | 65.3575 | 83.29 | 92 | 1668 | 65 | 421551 | 0.99 | 796.13 | 23.3656 | 83.29 | 3989.68 | 52033.09 | 67090.97 | VPC | 6.6193 | 107.3511 | 1946.3229 | 33.5868 | 2.3919 | 31.1949 | 2.7972 | 29.3509 | Level II (26-50) | Volume from own sources | Billed metered | Billed unmetered
USA-Hunter Army Airfield Main | GA 0510107 | Chatham | 7500 | 153.6 | 0.4 | Note 1 | 154 | 28 | 60.6 | Note 1 | 64 | 152.6 | 1.4 | 0.443 | 0.957 | 65.4 | 66.4 | 980 | 55 | 244431 | 15.92 | 1592 | 10.1624 | 65.4 | 7052.56 | 1523.54 | 110464.1 | VPC | 1.2385 | 2.6754 | 39.4867 | 8.7511 | 7.1965 | 1.5546 | 0.09417 | 60 | Tier III (51-70) | Billed Metered (BMAC) | Customer Metering Inaccuracies (CMI) | Billed Unmetered (BUAC)
USMC-Logistics Base Albany | GA0950035 | Dougherty | 3350 | 77.357 | Note 1 | Note 1 | 74.3817 | 26.962 | 17.205 | Note 1 | 0.92977 | 45.0968 | 29.285 | 0.5257 | 28.7593 | 30.2147 | 40.3 | 320 | 62.5 | 193837 | 0.32 | 361.15 | Note 3 | 30.21 | 168.22 | 10386.41 | 10890.42 | VPC | 4.5009 | 246.2265 | 1955.1485 | 32.9832 | 0.52569 | 32.4575 | Note 3 | 31.5739 | Level II (26-50) | Volume from own sources | Billed metered | Billed unmetered
USN-Kings Bay Submarine Base | GA0390013 | Camden | 1300 | 328.6 | Note 1 | Note 1 | 328.6 | 139.836 | 111.215 | 15.25 | 0.62763 | 266.9286 | 61.6714 | 18.487 | 43.1843 | 77.549 | 100 | 500 | 101 | 3500000 | 1.79 | 241.19 | 22.7088 | 77.549 | 30467.42 | 10415.63 | 44712.57 | VPC | 101.2988 | 236.6265 | 1183.1326 | 81.7661 | 60.9348 | 20.8313 | 1.9017 | 68 | Tier III (51-70) | Volume from Own Sources (VOS) | Billed Unmetered (BUAC) | Unauthorized Consumption (UC)
Utilities, Inc. (Big Canoe Subdivision) | GA2270004 | Pickens | 7522 | 230.974 | Note 1 | Note 1 | 231.208 | 103.36 | Note 1 | 3.128 | 0.2584 | 106.7464 | 124.4616 | 2.69 | 121.7716 | 127.848 | 94.2 | 3452 | 150 | 894257 | 5.63 | 2010.61 | 56.2514 | 127.848 | 14913.79 | 685573.97 | 719553.19 | CRUC | 2.135 | 96.6456 | 3541.6216 | 202.9223 | 4.3203 | 198.602 | 2.1648 | 73 | Tier IV (71-90) | Billed Metered (BMAC) | Volume from Own Sources (VOS) | Unauthorized Consumption (UC)
Valdosta | GA1850002 | Lowndes | 51769 | 2994.078 | Note 1 | 22.464 | 2971.614 | 2042.66 | Note 1 | 20.364 | 37.1452 | 2100.1692 | 871.4448 | 17.7062 | 853.7387 | 928.954 | 444 | 23443 | 63 | 5069057 | 2.47 | 170.58 | 136.0957 | 928.95 | 43788.96 | 145630.74 | 199229.62 | VPC | 2.0693 | 99.7743 | 5268.0406 | 8.08 | 1.8679 | 6.2121 | 6.2731 | 77.1014 | Level IV (75-90) | Volume from own sources | Unbilled metered | Total annual cost of operating water system
Vidalia | GA2790002 | Toombs | 13050 | 581.879 | Note 1 | Note 1 | 582.1701 | 397.351 | Note 1 | 100.034 | 7.2771 | 504.6621 | 77.508 | 12.5995 | 64.9084 | 184.8191 | 141 | 7064 | 47 | 1170643 | 2.63 | 226.7 | 31.2634 | 184.82 | 33136.73 | 14714.74 | 72178.9 | VPC | 4.8866 | 25.1743 | 1261.2152 | 6.774 | 4.6909 | 2.0831 | 2.0762 | 74.1891 | Level III (51-75) | Customer metering inaccuracies | Volume from own sources | Billed metered
Vienna | GA0930004 | Dooly | 4100 | 773.071 | Note 1 | Note 1 | 773.1483 | 567.008 | 2 | Note 1 | 1.4225 | 570.4305 | 202.7178 | 14.4166 | 188.3012 | 204.1403 | 76 | 1455 | 56 | Note 5 | 4.49 | 170.11 | 12.8651 | 204.1403 | 64730.68 | 32031.91 | 97004.57 | VPC | 27.1461 | 354.566 | 6788.0736 | 66.5035 | 44.4884 | 22.0151 | 14.6365 | 45 | Tier II (26-50) | Volume from Own Sources (VOS) | Billed Unmetered (BUAC) | Length of Mains (Lm)
Villa Rica | GA0450006 | Carroll | 16970 | 454.278 | 235.32 | Note 1 | 694.0719 | 523.546 | Note 1 | 1.987 | 1.3089 | 526.8419 | 167.23 | 10.6208 | 156.6093 | 170.5259 | 136.9 | 7019 | 83 | 1436068 | 6.94 | 1148.39 | 54.3334 | 170.5259 | 73532.9 | 179848.5 | 257166.34 | VPC | 4.1456 | 61.1293 | 3134.1595 | 36.0994 | 10.4763 | 25.6231 | 2.8824 | 63 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Billed Metered (BMAC)
Walker County Water & Sewerage Authority | GA2950003 | Walker | 36000 | 1488.798 | Note 1 | 368.978 | 1131.1313 | 589.882 | Note 1 | 3.573 | 14.1391 | 607.5941 | 523.5372 | 16.4139 | 507.1233 | 541.2493 | 429.4 | 11164 | 115 | 5662833.72 | 5.45 | 384 | 167.8015 | 541.25 | 89455.54 | 194735.35 | 290992.35 | VPC | 4.0281 | 124.4517 | 3235.6286 | 25.456 | 8.0129 | 17.4432 | 3.0222 | 61.8601 | Level III (51-75) | Volume from own sources | Unbilled metered | Water exported
Walthourville | GA1790020 | Liberty | 3858 | 133.06 | Note 1 | Note 1 | 133.06 | 60.707 | Note 1 | Note 1 | 0.15177 | 60.8588 | 72.2012 | 0.91674 | 71.2845 | 72.353 | 37 | 1772 | 145.3 | Note 5 | 9.54 | 830.32 | 24.7125 | 72.353 | 8745.67 | 59188.94 | 68060.63 | VPC | 1.4174 | 110.2144 | 5278.378 | 38.3378 | 4.9355 | 33.4023 | 2.8846 | 48 | Tier II (26-50) | Billed Metered (BMAC) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI)
Walton County Water Department | GA2970008 | Walton | 43534 | Note 1 | 2006.765 | 434.462 | 1588.1848 | 983.956 | Note 1 | Note 1 | 2.4599 | 986.4159 | 601.769 | 8.8714 | 592.8975 | 604.2288 | 604 | 29514 | 94 | 11000000 | 7.12 | 1350 | 278.3904 | 604.2288 | 63164.44 | 800411.69 | 866896.98 | VPC | 0.82352 | 55.0375 | 2689.3656 | 29.2599 | 2.1402 | 27.1197 | 2.1297 | 76 | Tier IV (71-90) | Water Imported (WI) | Unauthorized Consumption (UC) | Systematic Data Handling Errors (SDHE)
Warner Robins | GA1530007 | Houston | 80308 | 3022.8859 | 804.7934 | Note 1 | 3827.6793 | 2418.07 | Note 1 | Note 1 | 6.0452 | 2424.1152 | 1403.5641 | 86.876 | 1316.6881 | 1409.6093 | 482.73 | 28347 | 62 | 7215938 | 2.21 | 519.33 | 155.3237 | 1409.6093 | 191996 | 683795.62 | 878931.07 | VPC | 8.3965 | 127.2574 | 7472.8412 | 30.8954 | 6.7731 | 24.1223 | 8.4771 | 72 | Tier IV (71-90) | Water Imported (WI) | Customer Metering Inaccuracies (CMI) | Unauthorized Consumption (UC)
Washington | GA3170002 | Wilkes | 6490 | 332.56 | Note 1 | Note 1 | 332.4603 | 171.3 | Note 1 | Note 1 | 0.42825 | 171.7283 | 160.732 | 9.8723 | 150.8597 | 161.1603 | 129.17 | 2691 | 80 | 1155300 | 4.66 | 1594.7417 | 32.1918 | 161.1603 | 46004.87 | 240582.3 | 287270.11 | VPC | 10.051 | 153.5913 | 3199.7701 | 106.4984 | 17.0958 | 89.4026 | 4.6863 | 58 | Tier III (51-70) | Billed Metered (BMAC) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI)
Waycross Water System | GA2990002 | Ware | 19900 | 834.675 | Note 1 | Note 1 | 826.4109 | 811.7061 | Note 1 | 1.58 | 10.3301 | 823.6162 | 2.7947 | 4.0953 | -1.3006 | 14.7048 | 140 | 7446 | 48 | 1457104 | 1.5 | 166.09 | 32.8377 | 14.7 | 6131.56 | -216.02 | 7893.69 | VPC | 1.5068 | -0.47855 | -25.452 | 0.79446 | 0.82347 | -0.029012 | -0.039607 | 59.7686 | Level III (51-75) | Volume from own sources | Unbilled metered | Billed metered
Waynesboro | GA0330004 | Burke | 5813 | 284.458 | Note 1 | Note 1 | 278.8804 | 191.678 | Note 1 | 31.3 | 3.486 | 226.464 | 52.4164 | 5.727 | 46.6894 | 87.2024 | 59.4 | 2485 | 45 | 775500 | 5.05 | 1218.29 | 11.4007 | 87.2 | 28921.19 | 56881.25 | 128181.88 | VPC | 6.314 | 51.4753 | 2153.4717 | 34.5281 | 11.6383 | 22.8898 | 4.0953 | 61.0784 | Level III (51-75) | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered
West Point | GA2850002 | Troup | 4472 | 421.137 | 4.379 | 0.051 | 425.465 | 341.902 | Note 1 | Note 1 | 0.85475 | 342.7568 | 82.7082 | 6.9161 | 75.7921 | 83.563 | 85 | 2016 | 71 | 1874000 | 3.35 | 444.89 | 19.7537 | 83.563 | 30972.54 | 33719.15 | 65071.96 | VPC | 9.399 | 103.0008 | 2442.9365 | 32.0891 | 15.3634 | 16.7258 | 3.8369 | 61 | Tier III (51-70) | Volume from Own Sources (VOS) | Customer Metering Inaccuracies (CMI) | Variable Production Cost (VPC)
White County Water & Sewerage Authority | GA3110072 | White | 5811 | 313.401 | Note 1 | 116.917 | 190.7944 | 178.547 | Note 1 | Note 1 | 0.44637 | 178.9934 | 11.8011 | 3.6117 | 8.1893 | 12.2474 | 166.1 | 2652 | 100 | Note 5 | 5.18 | 184.33 | 47.3186 | 12.2474 | 18708.73 | 1509.54 | 20300.56 | VPC | 3.7312 | 8.4602 | 135.0786 | 7.6238 | 7.0546 | 0.56921 | 0.17307 | 76 | Tier IV (71-90) | Customer Metering Inaccuracies (CMI) | Water Exported (WE) | Unauthorized Consumption (UC)
Winder | GA0130002 | Barrow | 48000 | 1535.32 | 15.63 | 67.69 | 1483.26 | 1300.372 | Note 1 | 10.275 | 13.563 | 1324.21 | 159.05 | 19.6119 | 139.4381 | 182.888 | 418.04 | 17532 | 82 | 617619.42 | 6.39 | 402.27 | 146.3995 | 182.888 | 124704.38 | 56091.78 | 190385.47 | VPC | 3.0647 | 21.79 | 913.8415 | 10.3124 | 7.113 | 3.1994 | 0.95245 | 57 | Tier III (51-70) | Volume from Own Sources (VOS) | Variable Production Cost (VPC) | Billed Metered (BMAC)
Woodstock | GA0570003 | Cherokee | 29000 | 140.511 | 642.307 | 10.392 | 772.426 | 561.086 | Note 1 | 40.358 | 1.4027 | 602.8467 | 169.5793 | 4.3128 | 165.2665 | 211.34 | 103.3 | 7908 | 141.3 | 3501151 | 7.512 | 2774.82 | 90.0002 | 211.34 | 31918.66 | 458584.72 | 606381.85 | VPC | 1.4942 | 57.2566 | 4383.203 | 62.0262 | 4.0362 | 57.99 | 1.8363 | 73 | Tier IV (71-90) | Length of Mains (Lm) | Billed Metered (BMAC) | Volume from Own Sources (VOS)
Wrightsville | GA1670002 | Johnson | 3757 | 155.686 | Note 1 | Note 1 | 148.2724 | 115.021 | Note 1 | Note 1 | 1.8534 | 116.8744 | 31.398 | 12.0339 | 19.3641 | 33.2514 | 40.1 | 891 | 60 | 945025 | 1.87 | 0.79 | Note 3 | 33.25 | 22503.46 | 15.38 | 22520.3 | VPC | 37.003 | 59.5423 | 1322.9982 | 25.2737 | 25.2564 | 0.017262 | Note 3 | 58.1444 | Level III (51-75) | Volume from own sources | Billed metered | Customer metering inaccuracies
| Note 1 | “Note 1” represents N/A. The utility does not have uses that fit into this category.
| Note 2 | “Note 2” indicates the utility does not know what the value for this parameter is.
| Note 3 | “Note 3” indicates that the intended value cannot be calculated. The software does not display a value of UARL or ILI for very small water systems with low connection density or low pressure water distribution system. In summary, the UARL or ILI calculation has not yet been proven as fully valid for very small or low pressure water distribution systems.
| Note 4 | “Note 4” indicates that the intended value cannot be calculated. The software does not display a value for “Annual Cost of Real Losses” because the utility does not know what the value for the “variable production cost” is.
| Note 5 | “Note 5” indicates this input has been made optional in the new V6 software, as it is no longer used in calculating a Performance Indicator.
| Note A | Moody Air force Base only consumes its water and does no billing. They also randomly meter certain buildings. Most of the older buildings have no meter in place
| Note B | The variable production cost is not applicable to this utility. Water supply is entirely purchased as bulk water imported at a defined rate. No restriction applies for volume and there are no provisions on any rate adjustment for variable production cost. The City of Griffin does the entire meter reading for Spalding County. This cost is built in through a complex rate structure based on the contract between the County and City. In summary, Spalding County does not know the value for this field.
Yellow represents negative values (anomalies). Both the utilities and EPD are aware of these negative values (i.e. negative real losses and negative ILI values). These negative values are not credible. They are mostly due to extreme meter inaccuracies. For example, (a) over-estimation of authorized consumption, and/or (b) under-estimation of water supply, and/or (c) over-estimation of apparent losses. To resolve this issue, the utilities with negative values must (a) replace their old meters with new ones, and/or (b) perform high frequency (short intervals) recalibration and accuracy testing on a regular basis.